Series

OTP-F		Flexx Central Heat Pump and Cased Coil

Indoor Unit	          Indoor Unit         	         Outdoor Units

Cased Coil          	          Air Handler

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	24000, 36000, 42000, 60000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	Air Handler

-	Compact and space-saving design.

-	Compatible with most standard 24V thermostats on the market.

Cased Coil

- Two sizes available.

- Can be installed horizontally or vertically.

- Can be combined with a gas furnace or blower.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Smart pan heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-	Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 24.6 ft. (7.5 m).

- Flared connections.

Control 	-	Operating temperature:

-	 Cooling: -15 to 54 °C (5 to 129 °F).

- Heating: -30 to 24°C (-22 to 75 °F).

-	Temperature display format: °C or °F.

Warranty	-	10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

- Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	-	Private residence, condo, commercial building, office building, restaurant.

Models - Outdoor Unit

| Product # | FXD-ACD36 | FXD-ACD60 |
| --- | --- | --- |
| Qty |  |  |
| Technical Performance |
| Cooling capacity | Nominal | BTU/hr | 24000 | 36000 | 48000 | 54000 |
|  | Min. – max. | W (BTU/hr) | 3.2 - 10.8 (11000 - 37000) | 3.2 - 10.8 (11000 - 37000) | 9.96 - 14.65 (34000 - 50000) | 9.96 - 15.24 (34000 - 52000) |
| Heating capacity | Nominal | BTU/hr | 24000 | 36000 | 48000 | 54000 |
|  | Min. – max. | W (BTU/hr) | 2.9 - 11.1 (10000-38000) | 2.9 - 11.1 (10000-38000) | 10.26 - 16.12 (35000 - 55000) | 10.26 - 17.58 (35000 - 60000) |
| Power supply | V / Ph / Hz | 230/208 / 1 / 60 | 230/208 / 1 / 60 | 230/208 / 1 / 60 | 230/208 / 1 / 60 |
| SEER | - | 20 | 18 | 18 | 17 |
| HSPF | - | 10.5 | 10 | 10.5 | 10 |
| EER | - | 12.5 | 10 | 11.5 | 10.5 |
| COP | - | 4 | 3 | 3.26 | 3.46 |
| MCA | A | 24 | 24 | 35 | 35 |
| Max. over-current protection (MOCP) | A | 35 | 35 | 45 | 45 |
| AHRI number | - | 207497901 | 207497902 | 207497903 | 207497904 |
| ENERGY STAR | - | ( | - | - | - |
| Refrigerant volume (R410A) | lb | 9.3 | 9.3 | 12.3 | 12.3 |
| Connection pipes | Liquid | in. | 3/8 | 3/8 | 3/8 | 3/8 |
|  | Gas | in. | 3/4 | 3/4 | 3/4 | 3/4 |
| Net weight | lb (kg) | 217 (98.5) | 217 (98.5) | 308 (140) | 308 (140) |
| Sound level | dB (A) | 55 (45 - 56) | 57 (45 - 57) | 58 (48 - 61) | 58 (48 - 61) |
| Compressor power input | W | 3680 | 3680 | 6000 | 6000 |
| Compressor LRA | A | 16 | 16 | 19 | 19 |
| Compressor RLA | A | - | - | - | - |
| Fan motor power output | A | 1.5 | 1.5 | 1.5 x 2 | 1.5 x 2 |
| Dimension (L x H x l) | Product | in. | 37 x 32 1/4 x 18 1/8 | 37 x 32 1/4 x 18 1/8 | 39 3/8 x 53 3/4 x 14 1/2 | 39 3/8 x 53 3/4 x 14 1/2 |
|  | Package | in. | 42 x 38 5/16 x 22 9/16 | 42 x 38 5/16 x 22 9/16 | 45 x 59 3/8 x 18 7/8 | 45 x 59 3/8 x 18 7/8 |
| Used heating power input | Nominal | W | 1020 | 1100 | 1730 | 2000 |
|  | Min. – max. | W | 160 - 1350 | 400 - 1400 | 580 - 2600 | 450 - 3000 |
| Operating ambient temperature in cooling | °C (°F) | -15 to 54 (5 to 129) |
| Operating ambient temperature in heating | °C (°F) | -30 to 24 (-22 to 75) |
| Maximum pipe length between outdoor and indoor units | ft. (m) | 164 (50) | 164 (50) | 170 (52) | 170 (52) |
| Maximum height between outdoor and indoor units | ft. (m) | 49 (15) | 49 (15) | 49 (15) | 49 (15) |

Models - Indoor Unit (Air handler)

| Product # | AH224 | AH236 | AH248 | AH260 |
| --- | --- | --- | --- | --- |
| Qty |  |  |  |  |
| Electrical data | Power supply | V / Ph / Hz | 230/208 / 1 / 60 | 230/208 / 1 / 60 | 230/208 / 1 / 60 | 230/208 / 1 / 60 |
|  | Supply | Cooling | W | 145 | 180 | 300 | 420 |
|  | Input current | Cooling | A | 1.10 | 1.33 | 2.13 | 2.74 |
|  | Max. over-current protection (MOCP) | A | 15 | 15 | 15 | 15 |
|  | Voltage min./max. | V | 187 / 253 | 187 / 253 | 187 / 253 | 187 / 253 |
| Sound level | dB (A) | 55 | 57 | 58 | 61 |
| Refrigerant | Type | - | R410A |
|  | Control | - | Thermal expansion valve |
| ENERGY STAR | - | ( | - | - | - |
| Air flow | cfm | 960 | 1000 | 1380 | 1600 |
|  | m3/hr | 1630 | 1700 | 2350 | 2720 |
| HPS (High Static Pressure) | Nominal | Pa | 25 | 37 | 50 | 50 |
|  |  | inH2O | 0.1 | 0.148 | 0.2 | 0.2 |
|  | Range | Pa | 0 to 250 | 0 to 250 | 0 to 250 | 0 to 250 |
|  |  | inH2O | 0 to 1 | 0 to 1 | 0 to 1 | 0 to 1 |
| Fan motor | Model | - | B-FGZ370C | B-FGZ370C | B-FGZ750C | B-FGZ750C |
|  | Transmission type | - | Direct transmission |
|  | Speed | RPM | 750 | 820 | 840 | 920 |
|  | Electric power | W | 0.5 | 0.5 | 1 | 1 |
|  | Full load current (FLA) | A | 3 | 3 | 5 | 5 |
| Fan | Type | - | Centrifugal |
|  | Quantity | - | 1 |
| Evaporator | Material | - | Copper tube with inner groove – Aluminum fins |
|  | Surface area | sq. ft. (m²) | 4.09 (0.38) | 4.09 (0.38) | 5.49 (0.51) | 5.49 (0.51) |
|  | Pipe diameter | in. | 3/8 | 3/8 | 3/8 | 3/8 |
|  | Fins type | - | Hydrophilic |
|  | Dimension (L x H x l) | in. | 16 5/16 x 2 x 18 | 16 5/16 x 2 x 18 | 16 5/16 x 3 1/2 x 24 | 16 5/16 x 3 1/2 x 24 |
| Operating temperature (cooling) | °C (°F) | 18 to 27 (64.4 to 80.6) |
| System operation control | - | Wired controller |
| Dimension | Unit only (L x H x l) | in. | 21 1/4 x 48 1/4 x 21 1/4 | 21 1/4 x 48 1/4 x 21 1/4 | 24 3/4 x 57 x 21 1/4 | 24 3/4 x 57 x 21 1/4 |
|  |  | mm | 660 x 603 x 1280 | 660 x 603 x 1280 | 693 x 660 x 1508 | 693 x 660 x 1508 |
| Weight | Net | lb (kg) | 156 (71) | 156 (71) | 178 (81) | 178 (81) |
|  | Gross | lb (kg) | 170 (77) | 170 (77) | 192 (87) | 192 (87) |

Models - Indoor Unit (Cased Coil)

| Product # | Indoor Unit | GCAT24F/NAA | GCAT36F/NAA | GCAT48H/NAA | GCAT60H/NAA |
| --- | --- | --- | --- | --- | --- |
|  | Outdoor Unit | FXD-ACD36 | FXD-ACD36 | FXD-ACD60 | FXD-ACD60 |
| Qty |  |  |  |  |
| Technical Performance |
| Power supply | V / Ph / Hz | 208-230 / 1 / 60 |
| Cooling capacity | Nominal | W (BTU/hr) | 24000 | 36000 | 48000 | 54000 |
|  | Min. – max. | W (BTU/hr) | 3517 - 7034 (12000 - 24000) | 5275 - 10844 (18000 - 37000) | 9964 - 14067 (34000 - 48000) | 10257 - 15826 (35000 - 54000) |
| Heating capacity | Nominal | W (BTU/hr) | 24000 | 36000 | 48000 | 54000 |
|  | Min. – max. | W (BTU/hr) | 3517 - 8792 (12000-30000) | 5275 - 11137 (18000-38000) | 9964 - 15240 (34000 - 52000) | 10257 - 17584 (35000 - 60000) |
| SEER2 | - | 15.2 | 15.2 | 15.2 | 15.2 |
| HSPF2 | - | 8.5 | 8.5 | 8.5 | 8.5 |
| EER2 | W/W | 11 | 9.5 | 10 | 9.5 |
| COP | W/W | 4.2 | 3.5 | 3.6 | 3.5 |
| AHRI number | - | 213164338 | 213164339 | 213164340 | 213164341 |
| ENERGY STAR | - | YES | NO | NO | NO |
| Indoor Unit |
| Dehumidification | L/hr (pt/hr) | 2.85 (6.03) | 4.58 (9.68) | 4.70 (9.94) | 5.74 (12.13) |
| Air flow volume (Max) | cfm | 800 | 1000 | 1230 | 1510 |
| Product dimension (L x H x l) | in. (mm) | 17 1/2 x 23 x 21 1/4 (445 x 585 x 540) | 17 1/2 x 23 x 21 1/4 (445 x 585 x 540) | 24 1/2 x 28 1/2 x 21 1/4 (622 x 725 x 540) | 24 1/2 x 28 1/2 x 21 1/4 (622 x 725 x 540) |
| Package dimension (L x H x l) | in. (mm) | 21 x 25 13/16 x 27 1/8 (535 x 655 x 690) | 21 x 25 13/16 x 27 1/8 (535 x 655 x 690) | 28 1/8 x 31 5/16 x 27 1/8 (714 x 795 x 689) | 28 1/8 x 31 5/1 x 27 1/8 (714 x 795 x 689) |
| Refrigerant charge | oz | 8.8 | 8.8 | 8.8 | 8.8 |
| Weight | Net | lb (kg) | 64 (29) | 64 (29) | 95 (43) | 95 (43) |
|  | Gross | lb (kg) | 75 (34) | 75 (34) | 110 (50) | 110 (50) |
| Pre-charge length | ft. (m) | 31 (9.5) | 31 (9.5) | 31 (9.5) | 31 (9.5) |
| Additional refrigerant charge | oz/ft. (g/m) | 0.32 (29) | 0.32 (29) | 0.32 (29) | 0.32 (29) |
| Liquid pipe outer diameter | in. | 3/8 | 3/8 | 3/8 | 3/8 |
| Gas pipe outer diameter | in. | 3/4 | 3/4 | 3/4 | 3/4 |
| Maximum length between outdoor and indoor units | ft. (m) | 164 (50) | 164 (50) | 164 (50) | 164 (50) |
| Maximum pipe height between outdoor and indoor units | ft. (m) | 100 (30) | 100 (30) | 50 (15) | 50 (15) |

Options

| Product # Kit | Description | Qty |
| --- | --- | --- |
| OTP-21-4216-01 | Electric heater 10kW |  |
| OTP-21-4217-00 | Electric heater 15kW |  |
| OTP-21-4228-00 | Electric heater 20kW |  |
| OTP-FKCP | Refrigeration pipe bender |  |
| OTP-B04537 | Terminal block kit |  |
| OTP-R02P033 | 24V thermostat |  |
| SV-ALGS1727-3 | Aluminum ground stand 17 1/8" X 27" (2" X 3" Angle) |  |

| Outdoor Unit | A | B | C | D | E | G |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| FXD-ACD36 | 37 | 940 | 18 1/8 | 460 | 32 1/4 | 820 | 24 | 610 | 19 1/8 | 486 | 18 1/8 | 460 |
| FXD-ACD60 | 39 3/8 | 1000 | 14 1/2 | 368 | 53 3/4 | 1365 | 24 1/2 | 620 | 15 1/2 | 395 | 14 1/2 | 370 |

| Indoor Unit Air Handler | Dimensions |
| --- | --- |
|  | W | D | H | A | B |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| AH224 | 21 1/4 | 540 | 21 1/4 | 540 | 48 1/4 | 1225 | 11 5/8 | 295 | 20 | 508 |
| AH236 |  |  |  |  |  |  |  |  |  |  |
| AH248 | 24 3/4 | 630 | 21 1/4 | 540 | 57 | 1448 | 11 5/8 | 295 | 20 | 508 |
| AH260 |  |  |  |  |  |  |  |  |  |  |

| Indoor Unit Cased Coil | W | D | H | A | B |
| --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| GCAT24F-NAA | 17 ½ | 445 | 21 1/4 | 540 | 23 | 585 | 15 7/8 | 405 | 19 3/8 | 492 |
| GCAT36F-NAA |  |  |  |  |  |  |  |  |  |  |
| GCAT48H-NAA | 24 ½ | 622 | 21 1/4 | 540 | 28 ½ | 725 | 22 7/8 | 580 | 19 3/8 | 492 |
| GCAT60H-NAA |  |  |  |  |  |  |  |  |  |  |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |