Series

ELK-MI	Mineral Insulated (M.I.) Alloy 825 Cable Assembly

Single Conductor

Double Conductor

Features

Outer jacket	-	Alloy 825.

Assembly components             	- 	Alloy 825.

Bus wire	-	Conductor type might vary depending on model

(Nichrome, KP, Constantan, Alloy (30, 60, 90), Copper).

Cold lead length	-	6 ft. (1.8 m) cold lead includes 18 in. (45 cm) flexible cord.

Ambient temperature	-	-60 °C to +60 °C (-76 °F to +140 °F).

Maximum operating

temperature (power on)	-	700 °C (1292 °F).

Nominal voltage	-	Up to 600V.

Bending radius, minimum	- 	Diameter x 6.

Installation temperature,

minimum	-	-60 °C (-76 °F).

Classification	-	Class I, Division 2, Groups A, B, C, D.

-	Class II, Division 1, Groups E, F, G.

-	Class III, Division 1.

-	Class I, Zone 1, AEx/Ex d e IIC T1…T6.

Standards	- 	CSA C22.2 130-16.

- UL 60079-30-1.

Certification	-	FM 18 US0191X.

- FM 18 CA0089X.

Rating	- 	Moisture proof, may be immersed in fluids.

Warranty	-	1-year basic warranty on the heating cable.

Application	-	Temperature maintenance, silos, vessels, tanks, pipelines, chemical and petrochemical

industries, oil and gas industry, industrial processes, mobile processing 	facilities, vacuum

processes, freeze prevention.

Models

| Double Conductor |  |  |  |  |  |  |  |  |  |  |  |  | Single Conductor |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 300V |  |  |  |  |  | 600V |  |  |  |  |  |  | 600V |  |  |  |  |  |
| Product # | Dia. in. | Ω/ft. | Dia. mm | Ω/m | Conductor Type | Product # | Dia. in. | Ω/ft. |  | Dia. mm | Ω/m | Conductor Type | Product # | Dia. in. | Ω/ft. | Dia. mm | Ω/m | Type de conducteur |
| 11E0L-2S | 0.16 | 11 | 4.1 | 36.089 | Nichrome R | 11E0H-2S | 0.22 | 11 |  | 5.6 | 36.089 | Nichrome R | 30E1H-1S | 0.17 | 3 | 4.3 | 9.842 | Nichrome R |
| 90E1L-2S | 0.16 | 9 | 4.1 | 29.527 | Nichrome R | 90E1H-2S | 0.23 | 9 |  | 5.7 | 29.527 | Nichrome R | 20E1H-1S | 0.17 | 2 | 4.3 | 6.562 | Nichrome R |
| 75E1L-2S | 0.16 | 7.5 | 4.1 | 24.606 | Nichrome R | 75E1H-2S | 0.24 | 7.5 |  | 6.0 | 24.606 | Nichrome R | 19E1H-1S | 0.17 | 1.88 | 4.3 | 6.168 | Nichrome R |
| 60E1L-2S | 0.16 | 6 | 4.1 | 19.685 | Nichrome R | 60E1H-2S | 0.23 | 6 |  | 5.8 | 19.685 | Nichrome R | 16E1H-1S | 0.17 | 1.6 | 4.3 | 5.249 | Nichrome A |
| 50E1L-2S | 0.16 | 5 | 4.1 | 16.404 | Nichrome R | 40E1H-2S | 0.24 | 4 |  | 6.1 | 13.123 | Nichrome A | 13E1H-1S | 0.17 | 1.3 | 4.3 | 4.265 | Nichrome A |
| 40E1L-2S | 0.16 | 4 | 4.1 | 13.123 | Nichrome A | 30E1H-2S | 0.26 | 3 |  | 6.5 | 9.842 | Nichrome A | 12E1H-1S | 0.17 | 1.22 | 4.3 | 4.003 | Nichrome A |
| 32E1L-2S | 0.16 | 3.2 | 4.1 | 10.498 | KP | 20E1H-2S | 0.26 | 2 |  | 6.5 | 6.562 | Nichrome R | 10E1H-1S | 0.17 | 1 | 4.3 | 3.281 | KP |
| 27E1L-2S | 0.16 | 2.7 | 4.1 | 8.858 | KP | 14E1H-2S | 0.26 | 1.4 |  | 6.5 | 4.593 | Constantan | 85E2H-1S | 0.17 | 0.85 | 4.3 | 2.789 | KP |
| 25E1L-2S | 0.16 | 2.5 | 4.1 | 8.202 | Constantan | 10E1H-2S | 0.26 | 1 |  | 6.5 | 3.281 | KP | 70E2H-1S | 0.17 | 0.7 | 4.3 | 2.297 | Constantan |
| 20E1L-2S | 0.16 | 2 | 4.1 | 6.562 | Constantan | 70E2H-2S | 0.27 | 0.7 |  | 6.7 | 2.297 | Constantan | 50E2H-1S | 0.17 | 0.5 | 4.3 | 1.640 | Constantan |
| 17E1L-2S | 0.16 | 1.7 | 4.1 | 5.577 | Constantan | 50E2H-2S | 0.28 | 0.5 |  | 7.1 | 1.640 | Constantan | 38E2H-1S | 0.17 | 0.38 | 4.3 | 1.247 | Constantan |
| 14E1L-2S | 0.16 | 1.4 | 4.1 | 4.593 | Constantan | 30E2H-2S | 0.3 | 0.3 |  | 7.6 | 0.984 | Constantan | 30E2H-1S | 0.17 | 0.3 | 4.3 | 0.984 | Constantan |
| 10E1L-2S | 0.17 | 1 | 4.2 | 3.281 | Constantan | 23E2H-2S | 0.28 | 0.23 |  | 6.9 | 0.755 | Alloy 90 | 25E2H-1S | 0.17 | 0.25 | 4.3 | 0.820 | Constantan |
| 70E2L-2S | 0.18 | 0.7 | 4.3 | 2.297 | Constantan | 20E2H-2S | 0.26 | 0.2 |  | 6.5 | 0.656 | Alloy 90 | 20E2H-1S | 0.18 | 0.2 | 4.4 | 0.656 | Constantan |
| 50E2L-2S | 0.19 | 0.5 | 4.8 | 1.640 | Alloy 60 | 15E2H-2S | 0.27 | 0.15 |  | 6.7 | 0.492 | Alloy 90 | 17E2H-1S | 0.18 | 0.17 | 4.3 | 0.558 | Constantan |
| 30E2L-2S | 0.17 | 0.3 | 4.3 | 0.984 | Alloy 60 | 10E2H-2S | 0.28 | 0.1 |  | 7.1 | 0.328 | Alloy 60 | 15E2H-1S | 0.17 | 0.15 | 4.3 | 0.492 | Alloy 60 |
| 25E2L-2S | 0.17 | 0.25 | 4.3 | 0.820 | Alloy 60 | 70E3H-2S | 0.3 | 0.07 |  | 7.5 | 0.230 | Alloy 60 | 12E2H-1S | 0.17 | 0.12 | 4.3 | 0.394 | Alloy 60 |
| 20E2L-2S | 0.17 | 0.2 | 4.3 | 0.656 | Alloy 60 | 50E3H-2S | 0.31 | 0.05 |  | 7.9 | 0.164 | Alloy 60 | 10E2H-1S | 0.17 | 0.1 | 4.3 | 0.328 | Alloy 60 |
| 15E2L-2S | 0.18 | 0.15 | 4.4 | 0.492 | Alloy 60 | 40E3H-2S | 0.33 | 0.04 |  | 8.3 | 0.131 | Alloy 60 | 80E3H-1S | 0.17 | 0.08 | 4.3 | 0.262 | Alloy 60 |
| 10E2L-2S | 0.19 | 0.1 | 4.8 | 0.328 | Alloy 30 | 30E3H-2S | 0.35 | 0.03 |  | 8.8 | 0.098 | Alloy 60 | 70E3H-1S | 0.17 | 0.07 | 4.3 | 0.230 | Alloy 60 |
| 70E3L-2S | 0.21 | 0.07 | 5.2 | 0.230 | Alloy 30 | 20E3H-2S | 0.27 |  | 0.02 | 6.9 | 0.066 | Copper | 60E3H-1S | 0.17 | 0.06 | 4.3 | 0.197 | Alloy 60 |
| 50E3L-2S | 0.23 | 0.05 | 5.7 | 0.164 | Alloy 30 | 16E3H-2S | 0.28 |  | 0.016 | 7.1 | 0.052 | Copper | 40E3H-1S | 0.18 | 0.04 | 4.4 | 0.131 | Alloy 60 |
| - | - | - | - | - | - | 13E3H-2S | 0.29 |  | 0.013 | 7.4 | 0.043 | Copper | 30E3H-1S | 0.19 | 0.03 | 4.7 | 0.098 | Alloy 60 |
| - | - | - | - | - | - | 10E3H-2S | 0.3 |  | 0.01 | 7.6 | 0.033 | Copper | 20E3H-1S | 0.2 | 0.02 | 5.1 | 0.066 | Alloy 60 |
| - | - | - | - | - | - | - | - |  | - | - |  |  | 10E3H-1S | 0.17 | 0.01 | 4.3 | 0.033 | Copper |
| - | - | - | - | - | - | - | - |  | - | - |  | - | 65E4H-1S | 0.18 | 0.0065 | 4.3 | 0.021 | Copper |
| - | - | - | - | - | - | - | - |  | - | - |  | - | 40E4H-1S | 0.19 | 0.0041 | 4.8 | 0.013 | Copper |

Made to order product, standard production lead time of 6 weeks, please contact factory for design and quote.

Cold Lead Sizes

| Double Conductor |  |  |  |  | Single Conductor |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Size | Max. Current (A) |  | Gland Diameter (NPT) |  | Size | Max. Current (A) |  | Gland Diameter (NPT) |  |
| AWG | CEC | NEC | CEC | NEC | AWG | CEC | NEC | CEC | NEC |
| 14 | 15 | 25 | 1/2'' (12.7 mm) | 1/2'' (12.7 mm) | 14 | 20 | 30 | 1/2'' (12.7 mm) | 1/2'' (12.7 mm) |
| 12 | 20 | 30 |  |  | 12 | 25 | 40 |  |  |
| 10 | 30 | 40 |  |  | 10 | 40 | 55 |  |  |
| 8 | 50 | 55 |  |  | 8 | 70 | 75 |  |  |

Configurations

| Design B | Single conductor cold lead M.I. Heater with clean laser hot to cold on both ends. |
| --- | --- |
| Design D | Two conductor cold lead M.I. Heater with clean laser seal hot to cold on one end. Clean laser seal hot to hot at opposite ends. |
| Design E | Two conductor cold lead M.I. Heater with clean laser seal hot to cold on both ends. |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electricial Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |