[image: image1.jpg]/|
X/
VX))



[image: image3.jpg]VERSION AVAILABLE



[image: image4.jpg]




Approval Drawings

Series

OAC
Commercial Wall Fan Heater

[image: image5.jpg]@DUELLET



 


Features

Color
-
Standard: white, almond.


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, aluminum, 
semi-gloss black, sand.


-
Custom colors available upon request. 

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
18-gauge steel front cover.

-
Bottom air outlet.


-
High-limit temperature control with automatic reset.
Fan
-
Closed, factory-lubricated motor.


-
160 cfm fan (single unit: 55 dBA); 2 X 160 cfm fan (double unit: 58 dBA); 



3 X 160 cfm fan (triple unit: 61 dBA).



-
Fan delay purges heater of residual heat.

Heating element
-
Durable tubular heating element with fins.

Control
-
Built-in thermostat included with control knob or tamperproof.

· 24V relay, with or without transformer available.

Note: Thermostat is not included in heater with factory installed relay.

Any remote thermostat or relay must be connected to the heater control terminal block.

Installation
-
Minimum clearance from the floor and adjacent walls: 10 in. (25.4 cm).


-
Surface mounting box available.


- 
Semi recessed trim kit available.
Warranty
-
5-year warranty against defects.

Application
-
Apartment building, commercial building, entrance way, stairwell, garage.
.
[image: image2.jpg]410 mm

—161/8"
561 mm
o 221/16"
Front View
368 mm
212 mm 14716 51 mm
85/16" | ) 2"
74 mm KOE @22 mm
27/8" TopView KOE @7/8"
51 mm— 4 51 mm
o
KOE @22 mm
KOE @7/8"

Single Unit

33mm —
15/16"

Side View

55 mm
23/16"-]—

34 mm
15/16"

506 mm
197/8"

Side View (All Models)

810 mm 1227 mm
I 318" 48516" ——
+ v +
P P . A
Front View Front View
767 mm 1185 mm
303/16" [ 46 5/8"
Top View Top View

VWLV
Double Unit

Triple Unit

1 109 mm
45/16"

561 mm
221/16"

Surface

Required Wall
Depth Opening
104 mm
‘l 41/8"

Recessed

Installation
(All Models)




Models

	Product #1
	Qty
	Volts (ph)
	Watts
	BTU/hr
	Weight
	Unit

	
	
	
	
	
	lb
	kg
	

	OACU01502-T
	
	120 (1)
	1500
	5123
	24.0
	10.9
	single

	OACU02008-T
	
	208 (1)
	2000
	6830
	24.0
	10.9
	single

	OACU04008-T
	
	208 (1)
	4000
	13661
	24.0
	10.9
	single

	OACU04038-T
	
	208 (3)
	4000
	13661
	26.0
	12.0
	single

	OACU04808-T
	
	208 (1)
	4800
	16393
	24.0
	10.9
	single

	OACU05038-T
	
	208 (3)
	5000
	17076
	26.0
	12.0
	single

	OACU06038-T
	
	208 (3)
	6000
	20491
	54.0
	24.5
	double

	OACU08008-T
	
	208 (1)
	8000
	27321
	50.0
	22.7
	double

	OACU09038-T
	
	208 (3)
	9000
	30737
	90.0
	40.9
	triple

	OACU12008-T
	
	208 (1)
	12000
	40982
	90.0
	40.9
	triple

	OACU12038-T
	
	208 (3)
	12000
	40982
	90.0
	40.9
	triple

	OACU01500-T2
	
	240/208 (1)
	1500/1125
	5123/3842
	24.0
	10.9
	single

	OACU02000-T2
	
	240/208 (1)
	2000/1500
	6830/5123
	24.0
	10.9
	single

	OACU03000-T2
	
	240/208 (1)
	3000/2250
	10246/7684
	24.0
	10.9
	single

	OACU03030-T2
	
	240/208 (3)
	3000/2250
	10246/7684
	26.0
	12.0
	single

	OACU04000-T2
	
	240/208 (1)
	4000/3000
	13661/10246
	24.0
	10.9
	single

	OACU04030-T2
	
	240/208 (3)
	4000/3000
	13661/10246
	26.0
	12.0
	single

	OACU04800-T2
	
	240/208 (1)
	4800/3600
	16393/12295
	24.0
	10.9
	single

	OACU05030-T2
	
	240/208 (3)
	5000/3750
	17076/12807
	26.0
	12.0
	single

	OACU06000-T2
	
	240/208 (1)
	6000/4500
	20491/15368
	50.0
	22.7
	double

	OACU08000-T2
	
	240/208 (1)
	8000/6000
	27321/20491
	50.0
	22.7
	double

	OACU12000-T2
	
	240/208 (1)
	12000/9000
	40982/30737
	90.0
	40.9
	triple

	OACU01577-T
	
	277 (1)
	1500
	5123
	28.0
	12.7
	single

	OACU02077-T
	
	277 (1)
	2000
	6830
	28.0
	12.7
	single

	OACU03077-T
	
	277 (1)
	3000
	10246
	28.0
	12.7
	single

	OACU04077-T
	
	277 (1)
	4000
	13661
	28.0
	12.7
	single

	OACU04877-T
	
	277 (1)
	4800
	16393
	28.0
	12.7
	single

	OACU06077-T
	
	277 (1)
	6000
	20491
	55.0
	25.0
	double

	OACU08077-T
	
	277 (1)
	8000
	27321
	55.0
	25.0
	double

	OACU12077-T
	
	277 (1)
	12000
	40982
	90.0
	40.9
	triple

	OACU01504-T
	
	480 (1)
	1500
	5123
	28.0
	12.7
	single

	OACU02004-T
	
	480 (1)
	2000
	6830
	28.0
	12.7
	single

	OACU03004-T
	
	480 (1)
	3000
	10246
	28.0
	12.7
	single

	OACU03034-T
	
	480 (3)
	3000
	10246
	30.0
	14.0
	single

	OACU04004-T
	
	480 (1)
	4000
	13661
	28.0
	12.7
	single

	OACU04034-T
	
	480 (3)
	4000
	13661
	30.0
	14.0
	single

	OACU04804-T
	
	480 (1)
	4800
	16393
	28.0
	12.7
	single

	OACU05034-T
	
	480 (3)
	5000
	17076
	30.0
	14.0
	single

	OACU06004-T
	
	480 (1)
	6000
	20491
	55.0
	25.0
	double

	OACU08004-T
	
	480 (1)
	8000
	27321
	55.0
	25.0
	double

	OACU12004-T
	
	480 (1)
	12000
	40982
	90.0
	40.9
	triple

	OACU12034-T
	
	480 (3)
	12000
	40982
	90.0
	40.9
	triple


1 Built-in thermostat included with control knob or tamperproof. 

2 208V = 75% of wattage at 240V. 

Add "BL" for white, "AM" for almond. Upcharge available for optional colors shown in the color chart section.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	KIT-OAC-BS1
	-
	Surface mounting box, single unit
	

	KIT-OAC-BS1-1
	-
	Semi recessed 1 in. trim kit, single unit
	

	KIT-OAC-BS1-2
	-
	Semi recessed 2 in. trim kit, single unit
	

	KIT-OAC-BS2
	-
	Surface mounting box, double unit
	

	KIT-OAC-BS2-1
	-
	Semi recessed 1 in. trim kit, double unit
	

	KIT-OAC-BS2-2
	-
	Semi recessed 2 in. trim kit, double unit
	

	KIT-OAC-BS3
	-
	Surface mounting box, triple unit
	

	KIT-OAC-BS3-1
	-
	Semi recessed 1 in. trim kit, triple unit
	

	KIT-OAC-BS3-2
	-
	Semi recessed 2 in. trim kit, triple unit
	

	KIT-OAC-DIS203
	DIS203
	Disconnect switch, double-pole, 20A at 277V and less (80% = 16A)
	

	KIT-OAC-DIS403
	DIS403
	Disconnect switch, triple-pole, 40A at 600V max. (80% = 32A)
	

	KIT-OAC-DIS803
	DIS803
	Disconnect switch, triple-pole, 80A at 600V max. (80% = 64A)
	

	-
	IV
	Fan switch
	

	-
	OO
	On/Standby heating switch
	

	-
	R4
	24V control relay, without transformer
	

	-
	RT4
	24V control relay, with transformer
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
4 If the built-in thermostat is not required with the 24V control relay, remove the “-T” from the product number (E.g.: OACU04004-RT). 
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

