[image: image1.jpg]


[image: image3.jpg]VERSION AVAILABLE



[image: image4.jpg]




Approval Drawings

Series

OACP
Commercial Ceiling Fan Heater

[image: image5.jpg]@DUELLET



 

Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, aluminum, 
semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 1-phase.

Construction
-
18-gauge steel front cover.


-
High-limit temperature control with automatic reset.

Fan
-
Factory-lubricated motor (open and ventilated).


-
160 cfm fan (single unit: 55.5 dBA), 2 X 160 cfm fan (double unit: 58.5 dBA).


-
Fan delay purges heater of residual heat.
Heating element
-
Durable tubular heating element with fins.

Control
-
240/208V control circuit standard with contactor when needed 
(except 120V model).

· 24V relay, with or without transformer available.
· Built-in thermostat available.
Note: If an electronic thermostat is used, it must be compatible with forced-air heaters.
Any remote thermostat or relay must be connected to the heater control terminal block.
Installation
-
Maximum recommended installation height: 10 ft. (3 m).

-
Minimum clearance from adjacent walls: 10 in. (25.4 cm).


-
Surface mounting box available.


-
Adaptor for T-bar ceiling available.

Warranty
-
3-year warranty against defects.

Application
-
Apartment building, commercial building, drop ceiling, stairwell, garage.
[image: image2.jpg]410 mm

—161/8" 1
0
561 mm
.| 22116"
Front View
368 mm
212mm 14716"
85/16" T 51;"“
74 mm KOE @22 mm

27/8" TopView KOE @7/8"

51T mm
o

KOE @7/8"

Single Unit

KOE @22 mm

33mm — ¢
15/16"
Side View

55 mm
23/16"

34 mm|

15/16"

506 mm
197/8"

Side View (All Models)

810 mm
T 317/8"

. .

Front View

767 mm
303/16"

o o o

Top View

Double Unit

Required Ceiling
Depth Opening

— 104mm
—

Recessed

—
45/16"

-1

I*561 mm—
221/16"

Surface

Installation
(All Models)




Models

	Product #
	Qty
	Volts
	Watts
	BTU/hr
	Weight
	Unit

	
	
	
	
	
	lb
	kg
	

	OACP1502
	
	120
	1500
	5123
	24.0
	10.9
	single

	OACP2008
	
	208
	2008
	6820
	24.0
	10.9
	single

	OACP4008
	
	208
	4000
	13661
	24.0
	10.9
	single

	OACP4808
	
	208
	4800
	16393
	24.0
	10.9
	single

	OACP8008
	
	208
	8000
	27321
	50.0
	22.7
	double

	OACP1500
	
	240/208
	1500/11251
	5123/3842
	24.0
	10.9
	single

	OACP2000
	
	240/208
	2000/15001
	6830/5123
	24.0
	10.9
	single

	OACP3000
	
	240/208
	3000/22501
	10246/7684
	24.0
	10.9
	single

	OACP4000
	
	240/208
	4000/30001
	13661/10246
	24.0
	10.9
	single

	OACP4800
	
	240/208
	4800/36001
	16393/12295
	24.0
	10.9
	single

	OACP6000
	
	240/208
	6000/45001
	20491/15368
	50.0
	22.7
	double

	OACP8000
	
	240/208
	8000/60001
	27321/20491
	50.0
	22.7
	double

	OACP1507
	
	347
	1500
	5123
	28.0
	12.7
	single

	OACP2007
	
	347
	2000
	6830
	28.0
	12.7
	single

	OACP3007
	
	347
	3000
	10246
	28.0
	12.7
	single

	OACP4007
	
	347
	4000
	13661
	28.0
	12.7
	single

	OACP6007
	
	347
	6000
	20491
	50.0
	22.7
	double

	OACP8007
	
	347
	8000
	27321
	50.0
	22.7
	double

	OACP1504
	
	480
	1500
	5123
	28.0
	12.7
	single

	OACP2004
	
	480
	2000
	6830
	28.0
	12.7
	single

	OACP3004
	
	480
	3000
	10246
	28.0
	12.7
	single

	OACP4004
	
	480
	4000
	13661
	28.0
	12.7
	single

	OACP6004
	
	480
	6000
	20491
	50.0
	22.7
	double

	OACP8004
	
	480
	8000
	27321
	50.0
	22.7
	double

	OACP1506
	
	600
	1500
	5123
	28.0
	12.7
	single

	OACP2006
	
	600
	2000
	6830
	28.0
	12.7
	single

	OACP3006
	
	600
	3000
	10246
	28.0
	12.7
	single

	OACP4006
	
	600
	4000
	13661
	28.0
	12.7
	single

	OACP4806
	
	600
	4800
	16393
	28.0
	12.7
	single

	OACP6006
	
	600
	6000
	20491
	50.0
	22.7
	double

	OACP8006
	
	600
	8000
	27321
	50.0
	22.7
	double


Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	KIT-OAWH-BSA
	-
	Surface mounting box for an extruded aluminum front grille, single unit
	

	KIT-OAWH-BSA1-1
	-
	Semi recessed 1 in. trim kit for an extruded aluminum front grille, single unit
	

	KIT-OAWH-BSA1-2
	-
	Semi recessed 2 in. trim kit for an extruded aluminum front grille, single unit
	

	KIT-OAWH-BSA2
	-
	Surface mounting box for an extruded aluminum front grille, double unit
	

	KIT-OAWH-BSA2-1
	-
	Semi recessed 1 in. trim kit for an extruded aluminum front grille, double unit
	

	KIT-OAWH-BSA2-2
	-
	Semi recessed 2 in. trim kit for an extruded aluminum front grille, double unit
	

	KIT-OAC-BS1
	-
	Surface mounting box, single unit
	

	KIT-OAC-BS1-1
	-
	Semi recessed 1 in. trim kit, single unit
	

	KIT-OAC-BS1-2
	-
	Semi recessed 2 in. trim kit, single unit
	

	KIT-OAC-BS2
	-
	Surface mounting box, double unit
	

	KIT-OAC-BS2-1
	-
	Semi recessed 1 in. trim kit, double unit
	

	KIT-OAC-BS2-2
	-
	Semi recessed 2 in. trim kit, double unit
	

	KIT-OAC-DVA
	-
	Extruded aluminum front grille, single unit
	

	KIT-OAC-DVA2
	-
	Extruded aluminum front grille, double unit
	

	KIT-OACP-DIS202
	DIS202
	Disconnect switch, double-pole, 20A at 240V
	

	KIT-OACP-DIS402
	DIS402
	Disconnect switch, triple-pole, 40A at 600V
	

	KIT-OACP-DIS802
	DIS802
	Disconnect switch, triple-pole, 80A at 600V
	

	-
	IV
	Fan switch
	

	KIT-OACP-R
	R
	24V control relay, without transformer
	

	-
	RT
	24V control relay, with transformer
	

	KIT-OACP-T
	T
	Thermostat
	

	KIT-OACP-T-BAR
	-
	Adaptor for T-bar ceiling installation, 23 3/4 in. X 23 3/4 in. (602 mm X 602 mm), single unit
	

	KIT-OACP-T-BAR2
	-
	Adaptor for T-bar ceiling installation, 23 3/4 in. X 47 11/16 in. (602 mm X 1211 mm), double unit
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 208V = 75% of wattage at 240V.

2 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Add "BL" for white, "AM" for almond. Upcharge available for optional colors shown in the color chart section.

277V available upon request.
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

