[image: image1.jpg]


[image: image4.jpg]VERSION AVAILABLE



[image: image5.jpg]




Approval Drawings

Series

OAS
Commercial Industrial Suspended Unit Heater

[image: image6.jpg]@DUELLET



 


Features

Color
-
Standard: almond.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.


-
Some units may be field converted from 3 to 1-phase.

Construction
-
18 and 20-gauge steel.


-
Adjustable louvres to direct air flow.


-
High-limit temperature control with automatic reset.

Fan
-

Totally enclosed factory-lubricated ball bearing motor 



(except for 15 to 25kW at 208/240V).


-
58 dBA fan (2 to 10kW), 67 dBA fan (15 to 30kW) and 77 dBA fan (40 to 60kW).

· Thermally-protected motor mounted in cold compartment.

· Fan delay purges heater of residual heat.

Heating element
-
Tubular heating elements; stainless steel (2 to 10kW); finned steel (15 to 60kW).

· Concentric disposition of heating elements.

· Factory sealed element upon request.
Control
-
Factory-installed contactor and 240/208V control circuit standard 
(with transformer if necessary).


-
24V relay, with or without transformer available.


-
120V control circuit available.


- 
Built-in thermostat available.


Ouellet highly recommends to use a wall thermostat for greater comfort.

Any remote thermostat or relay must be connected to the heater control terminal block.

Installation
-

Not for residential use in the United States.
· Horizontal mounting: 


2 to 30kW: wall or ceiling using the supplied brackets which allow 360° rotation.



40 to 60kW: ceiling only secured by the supplied 4 hooks of suspension.

-
Vertical mounting (except option -MD):



2 to 60kW: using 4 threaded rods 1/2 in. X 13 UNC (not included). 

-
Diffuser cones available (except option -MD).


-
Maximum recommended height (horizontal): 2 to 10kW:  8 ft. (2.4 m),  



15 to 30kW: 10 ft. (3 m), 40 to 60kW: 15 ft. (4.5 m).


-
Protective screen allows minimum horizontal mounting height: 


Canada 2 to 30 kW: 24 in. (610 mm), 40 to 60kW: 8 ft. (2.4 m).



United States 2 to 30 kW 6 ft. (1.8 m), 40 to 60kW: 8 ft. (2.4 m).



-
30 °C (85 °F) maximum operating ambient temperature.

Warranty
-
3-year warranty against defects.

Application
-
Commercial hall, warehouse, stairwell, factory.
[image: image2.jpg]4 Threaded Rods

(1/2"-13 UNC) 2t0 10kW | 15t030kW | 40 to 60kW
(Not Included) - - -
D , mm n. mm n. mm n.
¢ Z A 309 [121/8| 444 [171/2] 585 | 23
B 419 [161/2] 556 | 217/8| 641 [251/4
g Glmin) C 432 | 17 | 572 [221/2| 870 [341/4
* D 357 [141/16| 470 [181/2| - -
" E 290 [117/16| 407 | 16 - -
F 490 [195/16] 630 |2413/16| 924 |363/8
G 305 | 12 | 305 | 12 | 305 | 12
F H 123 | 478 | 148 [513/16] 305 | 12
1 428 [167/8| 592 [23516] 890 | 35
v kg | b | kg | Ib | kg | Ib
* weighnt
// 20 | 45 39 | 85 68 | 150





[image: image3.jpg]Standard Installation

Small Area

=

Large Area

Motor in Cold S¢

Side View

O 2o
o]
o]
o]
By
Heating  Louvres
Elements
Fan
2t010kW | 15t030kW | 40 to 60kW
mm [ in. | mm | in. | mm | in.
A 305 | 12 | 444 [1712] 585 | 23
B | 419 [1612] 55 |217/8| 641 2514
C 432 | 17 | 572 |2212] 870 3418
D | 357 [1a16| 470 [1812] - | -
E | 200 [11706) 407 | 16 | - | -
F | 490 195716 630 241316 924 |3638
G 305 | 12 | 305 | 12 | 305 | 12
H [ 123|478 | 148 [51316| 305 | 12
|\ | 428 1678 592 23516 890 | 35
o ke | b | kg | b | kg | Ib
Weight 20 |45 | 39 | 85 | es | 150
4Threaded Rods
v, (1/2'-13UNO)
t (Not Included)
G (min)
F





Models

	Product # 
	Qty
	Volts
	Phase
	kW (BTU/hr)
	cfm
	Temperature Rise
	Motor

	
	
	
	
	
	
	oC
	oF
	HP
	rpm

	OASU05000AM-T2
	
	240
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07500AM-T2
	
	240
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10000AM-T2
	
	240
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU05034AM-T2
	
	480
	3
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07534AM-T2
	
	480
	3
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10034AM-T2
	
	480
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU02008
	
	208
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03008
	
	208
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04008
	
	208
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05008
	
	208
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU05038
	
	208
	3/11
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07538
	
	208
	3/11
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10008
	
	208
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU10038
	
	208
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15038
	
	208
	3
	15.0 (51180)
	1300
	20
	36
	1/8
	1550

	OASU20038
	
	208
	3
	20.0 (68240)
	1300
	27
	49
	1/8
	1550

	OASU25038
	
	208
	3
	25.0 (85300)
	1300
	34
	61
	1/8
	1550

	OASU02000
	
	240
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03000
	
	240
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04000
	
	240
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05000
	
	240
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU05030
	
	240
	3/11
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07500
	
	240
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU07530
	
	240
	3/11
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10000
	
	240
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU10030
	
	240
	3/11
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15030
	
	240
	3
	15.0 (51180)
	1300
	20
	36
	1/8
	1550

	OASU20030
	
	240
	3
	20.0 (68240)
	1300
	27
	49
	1/8
	1550

	OASU25030
	
	240
	3
	25.0 (85300)
	1300
	34
	61
	1/8
	1550

	OASU02077
	
	277
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03077
	
	277
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04077
	
	277
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05077
	
	277
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07577
	
	277
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU02034
	
	480
	3
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03034
	
	480
	3
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04034
	
	480
	3
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05034
	
	480
	3
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07534
	
	480
	3
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10034
	
	480
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15034
	
	480
	3
	15.0 (51180)
	1400
	19
	34
	1/3
	1725

	OASU20034
	
	480
	3
	20.0 (68240)
	1400
	25
	45
	1/3
	1725

	OASU25034
	
	480
	3
	25.0 (85300)
	1400
	31
	56
	1/3
	1725

	OASU30034
	
	480
	3
	30.0 (102360)
	1400
	38
	68
	1/3
	1725

	OASU40034
	
	480
	3
	40.0 (136480)
	2000
	35
	63
	3/4
	1140

	OASU50034
	
	480
	3
	50.0 (170600)
	2000
	44
	79
	3/4
	1140

	OASU60034
	
	480
	3
	60.0 (204720)
	2000
	53
	95
	3/4
	1140


1 Models with the indication "3/1" can be field converted from 3 to 1-phase.

2 Come with built-in thermostat.

Standard color is almond.

Add-MD to suffix for special Mine Duty Feature. 600V available upon request. 240V, 3-phase and 480V, 1-phase available upon request.

Remember to change the 3 for 0 when ordering. E.g.: OASU05034 becomes OASU05004.
Options
	Product #

Kit
	Product # 

Factory installed*
	Description
	Qty

	-
	120
	120V control circuit
	

	-
	3P
	Triple-pole contactor
	

	KIT-OAS-CD1AM
	-
	Diffuser cone, 2 to 10kW units
	

	KIT-OAS-CD2AM
	-
	Diffuser cone, 15 to 30kW units
	

	KIT-OAS-CD3AM
	-
	Diffuser cone, 40 to 60kW units
	

	-
	CV
	Summer fan switch, with motor 240V and 277V
	

	-
	CV
	Summer fan switch, with motor 480V and 600V
	

	-
	DIS403
	Disconnect switch, 40A
	

	-
	DIS803
	Disconnect switch, 80A
	

	-
	DIS1003
	Disconnect switch, 100A
	

	-
	ES1
	Factory sealed element
	

	-
	FANAM
	Fan blades with almond epoxy/polyester coating
	

	-
	MD2
	Mine duty
	

	
	MR
	High-limit temperature control with manual reset
	

	KIT-OAS-R
	R
	24V relay, without transformer
	

	-
	RCV240
	Summer fan relay 240V, remote control (switch not included)
	

	KIT-OAS-RT
	RT
	24V relay, with transformer
	

	
	SCCR14
	Fuse protected circuits for 100kA rated short circuit current (see available SCCR Options Chart)
	

	
	SCCR24
	Fuse protected circuits for 100kA rated short circuit current (see available SCCR Options Chart)
	

	
	SCCR34
	Fuse protected circuits for 100kA rated short circuit current (see available SCCR Options Chart)
	

	KIT-OAS-T
	T
	Thermostat
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 The option "sealed element" increases the reliability of these in humid environments. It does not completely eliminate the leakage currents of metal shealthed heating elements.
2 See features on the OAS-MD catalog page.
3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
4 The disconnect switch option cannot be used with the SCCR option.
SCCR Options Chart
	
	208V
	208V/3ph
	208V/3ph Convertible 3/1ph
	240V
	240V/

3ph convertible 3/1ph
	240V/3ph

Convertible 3/1ph
	277V
	347V
	480V
	480V/3ph
	600V
	600/3ph

	2kW
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1

	3kW
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1

	4kW
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1

	5kW
	SCCR1
	
	SCCR1
	SCCR1
	
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1

	7.5kW
	SCCR2
	
	SCCR3
	SCCR2
	
	SCCR3
	SCCR2
	SCCR1
	SCCR1
	SCCR1
	SCCR1
	SCCR1

	10kW
	SCCR2
	SCCR3
	
	SCCR2
	
	See note 1
	SCCR2
	SCCR1
	SCCR2
	SCCR1
	SCCR1
	SCCR1

	15kW
	SCCR2
	SCCR3
	
	SCCR2
	SCCR3
	
	
	
	See note 1
	SCCR1
	SCCR2
	SCCR1

	20kW
	SCCR2
	SCCR3
	
	SCCR2
	SCCR3
	
	
	
	See note 1
	SCCR1
	SCCR2
	SCCR1

	25kW
	SCCR2
	SCCR3
	
	SCCR2
	SCCR3
	
	
	
	
	SCCR3
	See note1
	SCCR1

	30kW
	
	
	
	
	
	
	
	
	
	SCCR3
	
	SCCR3

	40kW
	
	
	
	
	
	
	
	
	
	See note1
	
	See note1

	50kW
	
	
	
	
	
	
	
	
	
	See note1
	
	See note1

	60kW
	
	
	
	
	
	
	
	
	
	See note1
	
	See note1


1  Factory Installed SCCR Option is not available for these models. It requires the installation of an external fused Safety Switch (Not supplied by Ouellet).

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

