[image: image1.jpg]


[image: image4.jpg]@DUELLET



[image: image4.jpg]

Approval Drawings

Series

OAS
Commercial Industrial Suspended Unit Heater
[image: image5.jpg]VERSION AVAILABLE




[image: image6.jpg]


 

Features

Color
-
Standard: almond.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.


-
Some units may be field converted from 3 to 1-phase.

Construction
-
18 and 20-gauge steel.


-
Adjustable louvres to direct air flow.


-
High-limit temperature control with automatic reset.

Fan
-

Totally enclosed factory-lubricated ball bearing motor 



(except for 15 to 25kW at 208/240V).


-
58 dBA fan (2 to 10kW), 67 dBA fan (15 to 30kW) and 77 dBA fan (40 to 60kW).

· Thermally-protected motor mounted in cold compartment.

· Fan delay purges heater of residual heat.

Heating element
-
Tubular heating elements; stainless steel (2 to 10kW); finned steel (15 to 60kW).

· Concentric disposition of heating elements.

· Factory sealed element upon request.
Control
-
Factory-installed contactor and 240/208V control circuit standard 
(with transformer if necessary).


-
24V relay, with or without transformer available.


-
120V control circuit available.

- 
Built-in thermostat available.

Ouellet highly recommends to use a wall thermostat for greater comfort.
Any remote thermostat or relay must be connected to the heater control terminal block.
Installation
-

Not for residential use in the United States.
· Horizontal mounting: 


2 to 30kW: wall or ceiling using the supplied brackets which allow 360° rotation.


40 to 60kW: ceiling only secured by the supplied 4 hooks of suspension.

-
Vertical mounting (except option -MD):



2 to 60kW: using 4 threaded rods 1/2 in. X 13 UNC (not included). 

-
Diffuser cones available (except option -MD).


-
Maximum recommended height (horizontal): 2 to 10kW:  8 ft. (2.4 m),  



15 to 30kW: 10 ft. (3 m), 40 to 60kW: 15 ft. (4.5 m).


-
Protective screen allows minimum horizontal mounting height: 


Canada 2 to 30 kW: 24 in. (610 mm), 40 to 60kW: 8 ft. (2.4 m).



United States 2 to 30 kW 6 ft. (1.8 m), 40 to 60kW: 8 ft. (2.4 m).


-
30 °C (85 °F) maximum operating ambient temperature.

Warranty
-
3-year warranty against defects.

Application
-
Commercial hall, warehouse, stairwell, factory.
[image: image2.jpg]4 Threaded Rods

(1/2"-13 UNC) 2t0 10kW | 15t030kW | 40 to 60kW
(Not Included) - - -
D , mm n. mm n. mm n.
¢ Z A 309 [121/8| 444 [171/2] 585 | 23
B 419 [161/2] 556 | 217/8| 641 [251/4
g Glmin) C 432 | 17 | 572 [221/2| 870 [341/4
* D 357 [141/16| 470 [181/2| - -
" E 290 [117/16| 407 | 16 - -
F 490 [195/16] 630 |2413/16| 924 |363/8
G 305 | 12 | 305 | 12 | 305 | 12
F H 123 | 478 | 148 [513/16] 305 | 12
1 428 [167/8| 592 [23516] 890 | 35
v kg | b | kg | Ib | kg | Ib
* weighnt
// 20 | 45 39 | 85 68 | 150





[image: image3.jpg]Standard Installation

Small Area

=

Large Area

Motor in Cold S¢

Side View

O 2o
o]
o]
o]
By
Heating  Louvres
Elements
Fan
2t010kW | 15t030kW | 40 to 60kW
mm [ in. | mm | in. | mm | in.
A 305 | 12 | 444 [1712] 585 | 23
B | 419 [1612] 55 |217/8| 641 2514
C 432 | 17 | 572 |2212] 870 3418
D | 357 [1a16| 470 [1812] - | -
E | 200 [11706) 407 | 16 | - | -
F | 490 195716 630 241316 924 |3638
G 305 | 12 | 305 | 12 | 305 | 12
H [ 123|478 | 148 [51316| 305 | 12
|\ | 428 1678 592 23516 890 | 35
o ke | b | kg | b | kg | Ib
Weight 20 |45 | 39 | 85 | es | 150
4Threaded Rods
v, (1/2'-13UNO)
t (Not Included)
G (min)
F





Models

	Product # 
	Qty
	Volts
	Phase
	kW (BTU/hr)
	cfm
	Temperature Rise
	Motor

	
	
	
	
	
	
	oC
	oF
	HP
	rpm

	OASU05000AM-T2
	
	240
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07500AM-T2
	
	240
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10000AM-T2
	
	240
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU05034AM-T2
	
	480
	3
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07534AM-T2
	
	480
	3
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10034AM-T2
	
	480
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU02008
	
	208
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03008
	
	208
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04008
	
	208
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05008
	
	208
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU05038
	
	208
	3/11
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07538
	
	208
	3/11
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10008
	
	208
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU10038
	
	208
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15038
	
	208
	3
	15.0 (51180)
	1300
	20
	36
	1/8
	1550

	OASU20038
	
	208
	3
	20.0 (68240)
	1300
	27
	49
	1/8
	1550

	OASU25038
	
	208
	3
	25.0 (85300)
	1300
	34
	61
	1/8
	1550

	OASU02000
	
	240
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03000
	
	240
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04000
	
	240
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05000
	
	240
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU05030
	
	240
	3/11
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07500
	
	240
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU07530
	
	240
	3/11
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10000
	
	240
	1
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU10030
	
	240
	3/11
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15030
	
	240
	3
	15.0 (51180)
	1300
	20
	36
	1/8
	1550

	OASU20030
	
	240
	3
	20.0 (68240)
	1300
	27
	49
	1/8
	1550

	OASU25030
	
	240
	3
	25.0 (85300)
	1300
	34
	61
	1/8
	1550

	OASU02077
	
	277
	1
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03077
	
	277
	1
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04077
	
	277
	1
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05077
	
	277
	1
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07577
	
	277
	1
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU02034
	
	480
	3
	2.0 (6824)
	510
	7
	13
	1/30
	1550

	OASU03034
	
	480
	3
	3.0 (10236)
	510
	10
	18
	1/30
	1550

	OASU04034
	
	480
	3
	4.0 (13648)
	510
	14
	25
	1/30
	1550

	OASU05034
	
	480
	3
	5.0 (17060)
	700
	13
	23
	1/30
	1550

	OASU07534
	
	480
	3
	7.5 (25590)
	700
	19
	34
	1/30
	1550

	OASU10034
	
	480
	3
	10.0 (34120)
	700
	25
	45
	1/30
	1550

	OASU15034
	
	480
	3
	15.0 (51180)
	1400
	19
	34
	1/3
	1725

	OASU20034
	
	480
	3
	20.0 (68240)
	1400
	25
	45
	1/3
	1725

	OASU25034
	
	480
	3
	25.0 (85300)
	1400
	31
	56
	1/3
	1725

	OASU30034
	
	480
	3
	30.0 (102360)
	1400
	38
	68
	1/3
	1725

	OASU40034
	
	480
	3
	40.0 (136480)
	2000
	35
	63
	3/4
	1140

	OASU50034
	
	480
	3
	50.0 (170600)
	2000
	44
	79
	3/4
	1140

	OASU60034
	
	480
	3
	60.0 (204720)
	2000
	53
	95
	3/4
	1140


1 Models with the indication "3/1" can be field converted from 3 to 1-phase.

2 Come with built-in thermostat.

Standard color is almond.

Add-MD to suffix for special Mine Duty Feature. 600V available upon request. 240V, 3-phase and 480V, 1-phase available upon request.

Remember to change the 3 for 0 when ordering. E.g.: OASU05034 becomes OASU05004.
Options
	Product #

Kit
	Product # 

Factory installed*
	Description
	Qty

	-
	120
	120V control circuit
	

	-
	3P
	Triple-pole contactor
	

	KIT-OAS-CD1AM
	-
	Diffuser cone, 2 to 10kW units
	

	KIT-OAS-CD2AM
	-
	Diffuser cone, 15 to 30kW units
	

	KIT-OAS-CD3AM
	-
	Diffuser cone, 40 to 60kW units
	

	-
	CV
	Summer fan switch, with motor 240V and 277V
	

	-
	CV
	Summer fan switch, with motor 480V and 600V
	

	-
	DIS403
	Disconnect switch, 40A
	

	-
	DIS803
	Disconnect switch, 80A
	

	-
	DIS1003
	Disconnect switch, 100A
	

	-
	ES1
	Factory sealed element
	

	-
	FANAM
	Fan blades with almond epoxy/polyester coating
	

	-
	MD2
	Mine duty
	

	
	MR
	High-limit temperature control with manual reset
	

	KIT-OAS-R
	R
	24V relay, without transformer
	

	-
	RCV240
	Summer fan relay 240V, remote control (switch not included)
	

	KIT-OAS-RT
	RT
	24V relay, with transformer
	

	KIT-OAS-T
	T
	Thermostat
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 The option "sealed element" increases the reliability of these in humid environments. It does not completely eliminate the leakage currents of metal shealthed heating elements.
2 See features below.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

