[image: image4.jpg]@DUELLET



[image: image4.jpg]

Approval Drawings

Series

OAWH
Architectural Aluminum Wall Fan Heater

[image: image1.jpg]1Y

)

=4




 [image: image2.jpg]




Features

Color
-
Standard: white, almond, metallic silver, bronze, metallic charcoal,



aluminum, semi-gloss black, sand.

-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.
Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
Extruded aluminum front grille, 1/8 in. (3.2 mm) thick. 


-
Bottom air outlet.


-
High-limit temperature control with automatic reset.

Fan
-
Closed, factory-lubricated motor.

· 160 cfm fan (single unit: 55 dBA); 2 X 160 cfm fan (double unit: 58 dBA); 


3 X 160 cfm (triple unit: 61 dBA).


-
Fan delay purges heater of residual heat.

Heating element
-
Durable tubular heating element with fins.

Control
-
Built-in tamperproof thermostat included.

· 24V relay, with or without transformer available.


Note: Thermostat is not included in heater with factory installed relay.


Any remote thermostat or relay must be connected to the heater control terminal block.
Installation
-
Minimum clearance from the floor and adjacent walls: 10 in. (25.4 cm).


-
Surface mounting box available.


- 
Semi recessed trim kit available.

Warranty
-
5-year warranty against defects.

Application 
-
Apartment building, commercial building, entrance way, stairwell, garage.

[image: image3.jpg]408 mm
r—161/16"—

=——1578mm
223/4"

Ee==——1£

FrontView

368 mm
14 7/16"

51 mm

o
KOE @22 mm
KOE @7/8"

Single Unit

40 mm—_r
19/16"
Side View
55 mm
23/16"
34 mm
15/16"
506 mm
197/8"

Side View (All Models)

810 mm

1227 mm

317/8"

48 5/16"

=————————————————"—°
————————- " —

Front View
767 mm

303/16" |

Top View

Front View
1185 mm
46 5/8"
o o o
Top View

il

WW

NAW

MW

VWAV AWV

Double Unit

Triple Unit

o 109 mm
[ 45/16"

584 mm
53"

Surface

Required Wall
Depth Opening
—104 mm
-I 41/8"

Recessed

Installation
(All Models)




Models

	Product #1
	Qty
	Volts (ph)
	Watts
	BTU/hr
	Weight
	Unit

	
	
	
	
	
	lb
	kg
	

	OAWH01502-TAV
	
	120 (1)
	1500
	5123
	24.0
	10.9
	single

	OAWH02008-TAV
	
	208 (1)
	2000
	6830
	24.0
	10.9
	single

	OAWH04008-TAV
	
	208 (1)
	4000
	13661
	24.0
	10.9
	single

	OAWH04038-TAV
	
	208 (3)
	4000
	13661
	28.0
	13.0
	single

	OAWH04808-TAV
	
	208 (1)
	4800
	16393
	24.0
	10.9
	single

	OAWH05038-TAV
	
	208 (3)
	5000
	17076
	28.0
	12.7
	single

	OAWH06038-TAV
	
	208 (3)
	6000
	20491
	56.0
	25.4
	double

	OAWH08008-TAV
	
	208 (1)
	8000
	27321
	50.0
	22.7
	double

	OAWH09038-TAV
	
	208 (3)
	9000
	30737
	90.0
	40.9
	triple

	OAWH12008-TAV
	
	208 (1)
	12000
	40982
	90.0
	40.9
	triple

	OAWH12038-TAV
	
	208 (3)
	12000
	40982
	90.0
	40.9
	triple

	OAWH01500-TAV2
	
	240/208 (1)
	1500/1125
	5123/3842
	24.0
	10.9
	single

	OAWH02000-TAV2
	
	240/208 (1)
	2000/1500
	6830/5123
	24.0
	10.9
	single

	OAWH03000-TAV2
	
	240/208 (1)
	3000/2250
	10246/7684
	24.0
	10.9
	single

	OAWH03030-TAV2
	
	240/208 (3)
	3000/2250
	10246/7684
	28.0
	13.0
	single

	OAWH04000-TAV2
	
	240/208 (1)
	4000/3000
	13661/10246
	24.0
	10.9
	single

	OAWH04030-TAV2
	
	240/208 (3)
	4000/3000
	13661/10246
	28.0
	13.0
	single

	OAWH04800-TAV2
	
	240/208 (1)
	4800/3600
	16393/12295
	24.0
	10.9
	single

	OAWH05030-TAV2
	
	240/208 (3)
	5000/3750
	17076/12807
	28.0
	12.7
	single

	OAWH06000-TAV2
	
	240/208 (1)
	6000/4500
	20491/15368
	50.0
	22.7
	double

	OAWH08000-TAV2
	
	240/208 (1)
	8000/6000
	27321/20491
	50.0
	22.7
	double

	OAWH12000-TAV2
	
	240/208 (1)
	12000/9000
	40982/30737
	90.0
	40.9
	triple

	OAWH01577-TAV
	
	277 (1)
	1500
	5123
	24.0
	10.9
	single

	OAWH02077-TAV
	
	277 (1)
	2000
	6830
	24.0
	10.9
	single

	OAWH03077-TAV
	
	277 (1)
	3000
	10246
	24.0
	10.9
	single

	OAWH04077-TAV
	
	277 (1)
	4000
	13661
	24.0
	10.9
	single

	OAWH04877-TAV
	
	277 (1)
	4800
	16393
	24.0
	10.9
	single

	OAWH06077-TAV
	
	277 (1)
	6000
	20491
	55.0
	25.0
	double

	OAWH08077-TAV
	
	277 (1)
	8000
	27321
	55.0
	25.0
	double

	OAWH12077-TAV
	
	277 (1)
	12000
	40982
	90.0
	40.9
	triple

	OAWH01504-TAV
	
	480 (1)
	1500
	5123
	28.0
	12.7
	single

	OAWH02004-TAV
	
	480 (1)
	2000
	6830
	28.0
	12.7
	single

	OAWH03004-TAV
	
	480 (1)
	3000
	10246
	32.0
	15.0
	single

	OAWH03034-TAV
	
	480 (3)
	3000
	10246
	32.0
	15.0
	single

	OAWH04004-TAV
	
	480 (1)
	4000
	13661
	28.0
	12.7
	single

	OAWH04034-TAV
	
	480 (3)
	4000
	13661
	32.0
	15.0
	single

	OAWH04804-TAV
	
	480 (1)
	4800
	16393
	28.0
	12.7
	single

	OAWH05034-TAV
	
	480 (3)
	5000
	17076
	32.0
	15.0
	single

	OAWH06004-TAV
	
	480 (1)
	6000
	20491
	55.0
	25.0
	double

	OAWH08004-TAV
	
	480  (1)
	8000
	27321
	55.0
	25.0
	double

	OAWH12004-TAV
	
	480 (1)
	12000
	40982
	90.0
	40.9
	triple

	OAWH12034-TAV
	
	480 (3)
	12000
	40982
	90.0
	40.9
	triple


1 Built-in tamperproof thermostat included. 

2 208V = 75% of wattage at 240V. 

Add "BL" for white, "AM" for almond, "AE" for metallic silver, "BZ" for bronze, "CM" for metallic charcoal, "AL" for aluminum, "NL" for semi-gloss black, «SA» for sand.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	KIT-OAWH-BSA
	-
	Surface mounting box, single unit
	 

	KIT-OAWH-BSA1-1
	-
	Semi recessed 1 in. trim kit, single unit
	

	KIT-OAWH-BSA1-2
	-
	Semi recessed 2 in. trim kit, single unit
	

	KIT-OAWH-BSA2
	-
	Surface mounting box, double unit
	

	KIT-OAWH-BSA2-1
	-
	Semi recessed 1 in. trim kit, double unit
	

	KIT-OAWH-BSA2-2
	-
	Semi recessed 2 in. trim kit, double unit
	

	KIT-OAWH-BSA3
	-
	Surface mounting box, triple unit
	

	KIT-OAWH-BSA3-1
	-
	Semi recessed 1 in. trim kit, triple unit
	

	KIT-OAWH-BSA3-2
	-
	Semi recessed 2 in. trim kit, triple unit
	

	KIT-OAWH-DIS203
	DIS203
	Disconnect switch, double-pole, 20A at 277V and less (80% = 16A)
	 

	KIT-OAWH-DIS403
	DIS403
	Disconnect switch, triple-pole, 40A at 600V max. (80% = 32A)
	 

	KIT-OAWH-DIS803
	DIS803
	Disconnect switch, triple-pole, 80A at 600V max. (80% = 64A)
	 

	-
	IV
	Fan switch
	 

	-
	R4
	24V control relay, without transformer
	 

	-
	RT4
	24V control relay, with transformer
	 


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

4 If the built-in thermostat is not required with the 24V control relay, remove the “-TAV” from the product number (E.g.: OAWH04004-RT). 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

