[image: image1.jpg]A\




[image: image4.jpg]VERSION AVAILABLE



[image: image5.jpg]




Approval Drawings

Series

OCA
Cabinet Unit Heater

[image: image6.jpg]@DUELLET



 

Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, aluminum, 
semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
18-gauge steel. 



-
Insulated casing for noise reduction.

-
Extruded aluminum bar grilles prevent insertion of foreign objects.


-
Field adaptable air inlet and outlet.


-
High-limit temperature control with automatic reset.


-
240V control circuit included.


-
Optional fresh air inlet damper.


-
Optional air ﬁlters.

Fan
-
Direct drive, variable speed squirrel-cage fan.


-
Fan delay.


-
240/208V factory-lubricated motor (1/15 HP).


-
2 speed-motor available (1600/1500 rpm).
Heating element
-
Durable tubular heating element with fins.

Length
-
Four cabinet lengths are available: 28 in. (711 mm), 48 in. (1219 mm), 



66 in. (1676 mm), 80 in. (2032 mm).

Control
-
Wide range of control available.

Ouellet highly recommends use of a wall thermostat for greater comfort.

Installation
-
Multi-position mounting (surface, semi-recessed, recessed).


-
Maximum recommended installation height: 10 ft. (3 m).


-
Recess trim kit available for recessed or semi-recessed units.


-
Sub-base and special back plate available.
Warranty
-
3-year warranty against defects.

Application
-
Hallway, entry way, exhibition center.

[image: image2.jpg]Installation
with Sub-Base

7

51 mm
D'y

254 mm
10"

Installation with Recess Trim Kit

51 mm
o

Recessed

51 mm
o

Semi-Recessed

,

Surface
Installation

686

27"

mm

Wall
Opening

KOE ©44-@35 mm
KOE @1 3/4"-@1 3/8"

Cabinet length +

254 mm (1")

KOE @28-@22 mm

— KOE @1 1/8"-@7/8"

m
6"

L39 mm

112"

Front View

KOE ©6.4 mm
51 if KOE @1/4 l
o
‘ /* 254 mm
o‘o' 10"
* A_—J L 64 mm ’
[ — 21/2"
157 mmi. 187 mm
63/16" 7 3/8"

Bottom View




[image: image3.jpg]KOE ©44-035 mm
KOE @1 3/4"-21 3/8" KOE @28-622 mm

— KOE®1 18078’

KOE @6.4 mm
KOE @1/4"
51 mm
o
686 mm Wall *
27 Opening Bl
1 -
: 2172
Length + 157 mm |
—39mm T 254mm() - 6ang — = 1% mm
o 738
FrontView Bottom View
Installation with Sub-Base Installation
7 7 7
51 mm 51 mm 51 mm
oF JF oF

T

Recessed Semi-Recessed Surface
Edi Installation
10"
Wall Mouting Ceiling
Top Bottom Mounting
L vt
Semi-Recessed Recessed
D Type Mounting Only
Wall
- -
- -
Semi-Recessed Recessed
D Type Mounting Only





Models

	Watts
	Product #
	BTU/hr
	pcm
	Length
	Weight

	Hi
	Lo
	208V
(3 ph)
	Qté
	240V
(1 ph)
	Qté
	240V
(3 ph)
	Qté
	347V
(1 ph)
	Qté
	480V
(3 ph)
	Qté
	600V
(3 ph)
	Qté
	Hi
	Lo
	Hi
	Lo
	in.
	mm
	lb
	kg

	2000
	1333
	OCA020381
	
	OCA02000
	
	OCA02030
	
	OCA02007
	
	OCA020341
	
	OCA020361
	
	6830
	4552
	250
	200
	28
	711
	115
	52,3

	3000
	1000
	OCA030381
	
	OCA03000
	
	OCA03030
	
	OCA03007
	
	OCA030341
	
	OCA030361
	
	10246
	3415
	250
	200
	28
	711
	115
	52,3

	4000
	2667
	OCA040381
	
	OCA04000
	
	OCA04030
	
	OCA04007
	
	OCA040341
	
	OCA040361
	
	13661
	9108
	250
	200
	28
	711
	115
	52,3

	5000
	3333
	OCA050381
	
	OCA05000
	
	OCA05030
	
	OCA05007
	
	OCA050341
	
	OCA050361
	
	17076
	11383
	250
	200
	28
	711
	115
	52,3

	6000
	4000
	OCA060381
	
	OCA06000
	
	OCA06030
	
	OCA06007
	
	OCA060341
	
	OCA060361
	
	20491
	13661
	250
	200
	28
	711
	115
	52,3

	8000
	4000
	OCA080381
	
	OCA08000
	
	OCA08030
	
	OCA08007
	
	OCA080341
	
	OCA080361
	
	27321
	13661
	500
	400
	48
	1219
	146
	66,4

	10000
	5000
	OCA100381
	
	OCA10000
	
	OCA10030
	
	OCA10007
	
	OCA100341
	
	OCA100361
	
	34152
	17076
	500
	400
	48
	1219
	146
	66,4

	12000
	6000
	OCA120381
	
	OCA12000
	
	OCA12030
	
	OCA12007
	
	OCA120341
	
	OCA120361
	
	40982
	20491
	500
	400
	48
	1219
	146
	66,4

	15000
	10000
	OCA150381
	
	OCA15000
	
	OCA15030
	
	-
	-
	OCA150341
	
	OCA150361
	
	51228
	34152
	750
	600
	66
	1676
	210
	95,5

	18000
	12000
	OCA180381
	
	OCA18000
	
	OCA18030
	
	-
	-
	OCA180341
	
	OCA180361
	
	61473
	40982
	750
	600
	66
	1676
	210
	95,5

	20000
	10000
	OCA200381
	
	OCA20000
	
	OCA20030
	
	-
	-
	OCA200341
	
	OCA200361
	
	68304
	34152
	1000
	800
	80
	2032
	240
	109,1

	24000
	12000
	OCA240381
	
	OCA24000
	
	OCA24030
	
	-
	-
	OCA240341
	
	OCA240361
	
	81964
	40982
	1000
	800
	80
	2032
	240
	109,1


1 1-phase available upon request (change the "3" for an "0" to the product number).

Add "BL" for white, "AM" for almond. Upcharge available for optional colors shown in the color chart section.

277V available upon request.
Options
	Product # 

Kit
	Product #

Factory installed*
	Description
	Qty

	-
	120
	120V control circuit 
	

	-
	3P
	Triple-pole contactor
	

	-
	AF1
	Fresh air inlet
	

	-
	AFM1
	Power-operated fresh air inlet
	

	-
	DIS404
	Disconnect switch, 40A
	

	-
	DIS80 4
	Disconnect switch, 80A
	

	-
	DIS100 4
	Disconnect switch, 100A
	

	-
	FUS
	Circuit protection fuse
	

	-
	HL2
	Hi/Lo power switch
	

	KIT-OCA-IV
	IV
	On/Auto fan switch
	

	-
	MR
	High-limit temperature control with manual reset
	

	KIT-OCA-OO
	OO
	On/Standby heating switch
	

	KIT-OCA-R
	R
	24V control relay, without transformer
	

	-
	RHL3
	24V Hi/Lo power relay, with transformer
	

	-
	ROO3
	24V On/Standby heating relay, with transformer
	

	KIT-OCA-RT
	RT
	24V control relay, with transformer
	

	-
	RV3
	24V fan relay, with transformer
	

	KIT-OCA-T-AV
	TAV
	Single-pole thermostat, tamperproof
	

	-
	T2S
	2-stage thermostat, tamperproof
	

	Recess trim kit, 2 in. (51 mm)

	KIT-OCA-CR-28
	-
	28 in. (711 mm) Models
	

	KIT-OCA-CR-48
	-
	48 in. (1219 mm) Models
	

	KIT-OCA-CR-66
	-
	66 in. (1676 mm) Models
	

	KIT-OCA-CR-80
	-
	80 in. (2032 mm) Models
	

	Special back plate

	KIT-OCA-DU-28
	-
	28 in. (711 mm) Models
	

	KIT-OCA-DU-48
	-
	48 in. (1219 mm) Models
	

	KIT-OCA-DU-66
	-
	66 in. (1676 mm) Models
	

	KIT-OCA-DU-80
	-
	80 in. (2032 mm) Models
	

	Air filter, wall installation only

	KIT-OCA-FI-28
	FI
	28 in. (711 mm) Models
	

	KIT-OCA-FI-48
	FI
	48 in. (1219 mm) Models
	

	KIT-OCA-FI-66
	FI
	66 in. (1676 mm) Models
	

	KIT-OCA-FI-80
	FI
	80 in. (2032 mm) Models
	

	Washable air filter, wall installation only

	KIT-OCA-FIW-28
	FIW
	28 in. (711 mm) Models
	

	KIT-OCA-FIW-48
	FIW
	48 in. (1219 mm) Models
	

	KIT-OCA-FIW-66
	FIW
	66 in. (1676 mm) Models
	

	KIT-OCA-FIW-80
	FIW
	80 in. (2032 mm) Models
	

	Sub-base, 2 in. (51 mm)

	KIT-OCA-SO-28
	-
	28 in. (711 mm) Models
	

	KIT-OCA-SO-48
	-
	48 in. (1219 mm) Models
	

	KIT-OCA-SO-66
	-
	66 in. (1676 mm) Models
	

	KIT-OCA-SO-80
	-
	80 in. (2032 mm) Models
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 Do not install a built-in thermostat with these options.

2 OCA06006, is not available with optional HL.

3 When one of these options is ordered, the heater control will automatically be shipped at 24V.

4 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary information
	Volts
	Phase
	Watts
	Length

mm/in.
	Information

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

