[image: image1.jpg]




Approval Drawings

Series

OCB
Heavy-Duty Aluminum Draft Barrier

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 

· Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 

aluminum, semi-gloss black, sand.
-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.
Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.
Construction
-
14-gauge (0.0787 in. [2 mm]) aluminum front cover.


-
18-gauge satin coat steel cabinet.


-
Full length built-in wireway.


-
Separate low voltage wireway (-WW) available.


-
Pencil-proof openings less than 1/4 in. (6.4 mm).


-
Front fresh air inlet; top warm air outlet.



- Bottom fresh air inlet available (-BAI).

-
Clean back available (-BD).

-
Linear high-limit temperature control with automatic reset.



-
End caps included.

Heating element
-
Stainless steel tubular heating element with aluminum ﬁns.

-
Floating heating elements on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 275W/ft.

-
Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control
-
Built-in thermostat available with a control knob or tamperproof (installed on the right end only).


-
Mechanical, electronic or pneumatic relays available



(installed on the right end only).


Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Heater must be installed at least 3 in. (76 mm) from ﬁnished ﬂoor (for -BAI option).

-
Mounting holes spaced on 1 in. (25.4 mm) intervals for ease of installation.


-
Wall or floor mounted installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit available.

Warranty
-
3-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center, private residence.

[image: image3.emf]








Average Standard Watt Density Models 275W/ft. 

	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	500
	500/375
	OCB0502
	
	OCB0508
	
	OCB0500
	
	OCB0507
	
	-
	-
	28
	711
	8.0
	3.6

	750
	750/563
	OCB0752
	
	OCB0758
	
	OCB0750
	
	OCB0757
	
	OCB0756
	
	38
	965
	10.8
	4.9

	1000
	1000/750
	OCB1002
	
	OCB1008
	
	OCB1000
	
	OCB1007
	
	OCB1006
	
	48 3/16
	1224
	13.7
	6.2

	1250
	1250/938
	OCB1252
	
	OCB1258
	
	OCB1250
	
	OCB1257
	
	OCB1256
	
	57 11/16
	1465
	16.4
	7.5

	1500
	1500/1125
	OCB1502
	
	OCB1508
	
	OCB1500
	
	OCB1507
	
	OCB1506
	
	66 7/16
	1687
	18.8
	8.6

	1750
	1750/1313
	-
	
	OCB1758
	
	OCB1750
	
	OCB1757
	
	OCB1756
	
	75 13/16
	1925
	21.5
	9.8

	2000
	2000/1500
	-
	
	OCB2008
	
	OCB2000
	
	OCB2007
	
	OCB2006
	
	84 9/16
	2148
	24.0
	10.9

	2250
	2250/1688
	-
	
	OCB2258
	
	OCB2250
	
	OCB2257
	
	OCB2256
	
	93 1/2
	2375
	26.5
	12.1

	2500
	2500/1875
	-
	
	OCB2508
	
	OCB2500
	
	OCB2507
	
	OCB2506
	
	102 5/8
	2606
	29.1
	13.2


Average Low Watt Density Models

	Product #1
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V2
	120V
	Qty
	208V
	Qty
	240/
208V
	Qty
	347V
	Qty
	600V
	Qty

	OCB020X-711
	28"

(711 mm)
	8.0 lb
(3.6 kg)
	100
	200
	200/150
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OCB030X-711
	
	
	150
	300
	300/225
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OCB040X-711
	
	
	200
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB030X-965
	38"

(965 mm)
	10.8 lb
(4.9 kg)
	100
	300
	300/225
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB045X-965
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB060X-965
	
	
	200
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB040X-1224
	48 3/16"

(1224 mm)
	13.7 lb
(6.2 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB060X-1224
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB080X-1224
	
	
	200
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB050X-1465
	57 11/16"

(1465 mm)
	16.4 lb
(7.5 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB075X-1465
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB100X-1465
	
	
	200
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB060X-1687
	66 7/16"

(1687 mm)
	18.8 lb
(8.6 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB090X-1687
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB120X-1687
	
	
	200
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB070X-1925
	75 13/16"

(1925 mm)
	21.5 lb
(9.8 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB105X-1925
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB140X-1925
	
	
	200
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB080X-2148
	84 9/16"

(2148 mm)
	24.0 lb
(10.9 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB120X-2148
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB160X-2148
	
	
	200
	1600
	1600/1200
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB090X-2375
	93 1/2"

(2375 mm)
	26.5 lb
(12.1 kg)
	100
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB135X-2375
	
	
	150
	1350
	1350/1013
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB180X-2375
	
	
	200
	1800
	1800/1350
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB100X-2606
	102 5/8"

(2606 mm)
	29.1 lb
(13.2 kg)
	100
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB150X-2606
	
	
	150
	1500
	1500/1125
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB200X-2606
	
	
	200
	2000
	2000/1500
	-----
	-----
	(
	
	(
	
	(
	
	(
	


1 X = 2 (120V), 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
2 208V = 75% of wattage at 240V.
( = Available.
Add "BL" for white, "AM" for almond.
Other colors, accessories and finishes are available upon request. Please contact your customer service representative.
Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BAI
	Bottom fresh air inlet
	

	-
	BD1
	Clean back
	

	KIT-OCB-CE
	-
	Outside corner, 6 in. (152 mm)
	

	KIT-OCB-CI
	-
	Inside corner, 6 in. (152 mm)
	

	KIT-OCB-JT
	-
	Splice plate, 1 3/16 in. (30 mm)
	

	KIT-OCB-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 1 3/16 po (30 mm)
	

	KIT-OCB-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-OCB-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	OCB-SV-XX
	-
	Empty cabinet with length of XX mm (minimum: 154 mm, maximum: 2606 mm)
	

	Controls
	
	
	

	KIT-OCB-DIS203
	DIS203
	Disconnect switch, 20A à 277V max.
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-OCB-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OCB-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-OCB-RT-120
	RT
	Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V
	

	KIT-OCB-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-OCB-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-OCB-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-OCB-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-OCB-RT-6002
	RT2
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-OCB-T
	T
	Single-pole thermostat: 30A at 120V, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-T24
	T24
	Double-pole thermostat: 30A at 120, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-T-AV
	TAV
	Single-pole tamperproof thermostat: 30A at 120V, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-T2-AV4
	T2AV4
	Double-pole tamperproof thermostat: 30A at 120, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-OCB-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-OCB-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	-
	WW
	24V wireway
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 For anodized aluminum heaters, the clean back option will be fixed with visible rivets.

2 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

4 "Off" position.
Others

	Type
	Quantity
	Model and description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

