[image: image1.jpg]




Approval Drawings

Series

OCB
Heavy-Duty Aluminum Draft Barrier

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 

· Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 

aluminum, semi-gloss black, sand.
-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.
Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.
Construction
-
14-gauge (0.0787 in. [2 mm]) aluminum front cover.


-
18-gauge satin coat steel cabinet.


-
Full length built-in wireway.


-
Separate low voltage wireway (-WW) available.


-
Pencil-proof openings less than 1/4 in. (6.4 mm).


-
Front fresh air inlet; top warm air outlet.



- Bottom fresh air inlet available (-BAI).

-
Clean back available (-BD).

-
Linear high-limit temperature control with automatic reset.



-
End caps included.

Heating element
-
Stainless steel tubular heating element with aluminum ﬁns.

-
Floating heating elements on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 275W/ft.

-
Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control
-
Built-in thermostat available with a control knob or tamperproof (installed on the right end only).


-
Mechanical, electronic or pneumatic relays available



(installed on the right end only).


Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Heater must be installed at least 3 in. (76 mm) from ﬁnished ﬂoor (for -BAI option).

-
Mounting holes spaced on 1 in. (25.4 mm) intervals for ease of installation.


-
Wall or floor mounted installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit available.

Warranty
-
1-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center, private residence.

[image: image3.emf]








Average Standard Watt Density Models 275W/ft. 

	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	277V
	Qty
	480V
	Qty
	in.
	mm
	lb
	kg

	500
	500/375
	OCB0502
	
	OCB0508
	
	OCB0500
	
	OCB0577
	-
	-
	-
	28
	711
	8.0
	3.6

	750
	750/563
	OCB0752
	
	OCB0758
	
	OCB0750
	
	OCB0777
	
	OCB0754
	
	38
	965
	10.8
	4.9

	1000
	1000/750
	OCB1002
	
	OCB1008
	
	OCB1000
	
	OCB1077
	
	OCB1004
	
	48 3/16
	1224
	13.7
	6.2

	1250
	1250/938
	OCB1252
	
	OCB1258
	
	OCB1250
	
	OCB1277
	
	OCB1254
	
	57 11/16
	1465
	16.4
	7.5

	1500
	1500/1125
	OCB1502
	
	OCB1508
	
	OCB1500
	
	OCB1577
	
	OCB1504
	
	66 7/16
	1687
	18.8
	8.6

	1750
	1750/1313
	-
	
	OCB1758
	
	OCB1750
	
	OCB1777
	
	OCB1754
	
	75 13/16
	1925
	21.5
	9.8

	2000
	2000/1500
	-
	
	OCB2008
	
	OCB2000
	
	OCB2077
	
	OCB2004
	
	84 9/16
	2148
	24.0
	10.9

	2250
	2250/1688
	-
	
	OCB2258
	
	OCB2250
	
	OCB2277
	
	OCB2254
	
	93 1/2
	2375
	26.5
	12.1

	2500
	2500/1875
	-
	
	OCB2508
	
	OCB2500
	
	OCB2577
	
	OCB2504
	
	102 5/8
	2606
	29.1
	13.2


Average Low Watt Density Models

	Product #1
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V2
	120V
	Qty
	208V
	Qty
	240/
208V
	Qty
	277V
	Qty
	480V
	Qty

	OCB020X-711
	28"

(711 mm)
	8.0 lb
(3.6 kg)
	100
	200
	200/150
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OCB030X-711
	
	
	150
	300
	300/225
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OCB040X-711
	
	
	200
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB030X-965
	38"

(965 mm)
	10.8 lb
(4.9 kg)
	100
	300
	300/225
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB045X-965
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB060X-965
	
	
	200
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB040X-1224
	48 3/16"

(1224 mm)
	13.7 lb
(6.2 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB060X-1224
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB080X-1224
	
	
	200
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB050X-1465
	57 11/16"

(1465 mm)
	16.4 lb
(7.5 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	OCB075X-1465
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB100X-1465
	
	
	200
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB060X-1687
	66 7/16"

(1687 mm)
	18.8 lb
(8.6 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB090X-1687
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB120X-1687
	
	
	200
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB070X-1925
	75 13/16"

(1925 mm)
	21.5 lb
(9.8 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB105X-1925
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB140X-1925
	
	
	200
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB080X-2148
	84 9/16"

(2148 mm)
	24.0 lb
(10.9 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB120X-2148
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB160X-2148
	
	
	200
	1600
	1600/1200
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB090X-2375
	93 1/2"

(2375 mm)
	26.5 lb
(12.1 kg)
	100
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB135X-2375
	
	
	150
	1350
	1350/1013
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB180X-2375
	
	
	200
	1800
	1800/1350
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB100X-2606
	102 5/8"

(2606 mm)
	29.1 lb
(13.2 kg)
	100
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	OCB150X-2606
	
	
	150
	1500
	1500/1125
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	OCB200X-2606
	
	
	200
	2000
	2000/1500
	-----
	-----
	(
	
	(
	
	(
	
	(
	


1 X = 2 (120V), 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
2 208V = 75% of wattage at 240V.
( = Available.

Add "BL" for white, "AM" for almond. Upcharge available for optional colors shown in the color chart section.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.
Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BAI
	Bottom fresh air inlet
	

	-
	BD1
	Clean back
	

	KIT-OCB-CE
	-
	Outside corner, 6 in. (152 mm)
	

	KIT-OCB-CI
	-
	Inside corner, 6 in. (152 mm)
	

	KIT-OCB-JT
	-
	Splice plate, 1 3/16 in. (30 mm)
	

	KIT-OCB-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 1 3/16 po (30 mm)
	

	KIT-OCB-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-OCB-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	OCB-SV-XX
	-
	Empty cabinet with length of XX mm (minimum: 154 mm, maximum: 2606 mm)
	

	Controls
	
	
	

	KIT-OCB-DIS203
	DIS203
	Disconnect switch, 20A à 277V max.
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-OCB-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OCB-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-OCB-RT-120
	RT
	Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V 
	

	KIT-OCB-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-OCB-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-OCB-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-OCB-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-OCB-RT-6002
	RT2
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-OCB-T
	T
	Single-pole thermostat: 30A at 120V, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-T24
	T24
	Double-pole thermostat: 30A at 120V, 208V, 240V - 15A at 347V, 600V
	

	KIT-OCB-T-AV
	TAV
	Single-pole tamperproof thermostat: 30A at 120V, 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OCB-T2-AV4
	T2AV4
	Double-pole tamperproof thermostat: 30A at 120V, 208V, 240V - 15A at 347V, 600V
	

	KIT-OCB-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-OCB-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-OCB-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	-
	WW
	24V wireway
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 For anodized aluminum heaters, the clean back option will be fixed with visible rivets.

2 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

4 "Off" position.
Others

	Type
	Quantity
	Model and description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

