[image: image1.jpg]




Approval Drawings

Series

ODBA
Steel Draft Barrier

[image: image5.jpg]@DUELLET



     [image: image2.emf]







[image: image3.jpg]




Features

Color 
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 



aluminum, semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.

Construction
-
16-gauge steel front cover.


-
18-gauge satin coat steel cabinet.


-
Screw assembly for added strength.


-
Full length built-in wireway.


-
Front fresh air inlet; top warm air outlet.



- Bottom fresh air inlet available (-BAI).

-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset. 
High altitude version available (-HA).


-
End caps included. 

Heating element
-
Stainless steel tubular heating element with aluminum ﬁns.

-
Floating heating element on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 275W/ft.


-
Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control
-
Built-in thermostat available with a control knob 



or tamperproof.

· Mechanical, electronic or pneumatic relays available 


(installed on the right end only).

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Heater must be installed at least 2 in. (51 mm) from finished floor 



(for -BAI option).


-

Mounting holes spaced on 4 in. (102 mm) intervals for ease of installation.


-
Wall or floor mounted installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit available.

Warranty
-
3-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center, private residence.

[image: image4.emf]








Average Standard Watt Density Models 275W/ft.1
	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	500
	500/375
	ODBA0502
	
	ODBA0508
	
	ODBA0500
	
	ODBA0507
	
	-
	-
	28 7/8
	733
	10.5
	4.8

	750
	750/563
	ODBA0752
	
	ODBA0758
	
	ODBA0750
	
	ODBA0757
	
	ODBA0756
	
	38 7/8
	987
	12.7
	5.8

	1000
	1000/750
	ODBA1002
	
	ODBA1008
	
	ODBA1000
	
	ODBA1007
	
	ODBA1006
	
	49 1/8
	1248
	14.9
	6.8

	1250
	1250/938
	ODBA1252
	
	ODBA1258
	
	ODBA1250
	
	ODBA1257
	
	ODBA1256
	
	58 5/8
	1489
	17.0
	7.7

	1500
	1500/1125
	ODBA1502
	
	ODBA1508
	
	ODBA1500
	
	ODBA1507
	
	ODBA1506
	
	67 5/16
	1710
	18.8
	8.5

	1750
	1750/1313
	-
	-
	ODBA1758
	
	ODBA1750
	
	ODBA1757
	
	ODBA1756
	
	76 5/8
	1947
	20.8
	9.4

	2000
	2000/1500
	-
	-
	ODBA2008
	
	ODBA2000
	
	ODBA2007
	
	ODBA2006
	
	85 7/16
	2170
	22.7
	10.3

	2250
	2250/1688
	-
	-
	ODBA2258
	
	ODBA2250
	
	ODBA2257
	
	ODBA2256
	
	94 5/16
	2395
	24.6
	11.2

	2500
	2500/1875
	-
	-
	ODBA2508
	
	ODBA2500
	
	ODBA2507
	
	ODBA2506
	
	103 7/16
	2627
	26.6
	12.1


Average Low Watt Density Models

	Product #3
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V2
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty

	ODBA020X-733
	28 7/8"

(733 mm)
	11.6 lb
(5.3 kg)
	100
	200
	200/150
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODBA030X-733
	
	
	150
	300
	300/225
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODBA040X-7331
	
	
	200
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA030X-987
	38 7/8"

(987 mm)
	15.1 lb
(6.9 kg)
	100
	300
	300/225
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA045X-987
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA060X-9871
	
	
	200
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA040X-1248
	49 1/8"

(1248 mm)
	18.7 lb
(8.5 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA060X-1248
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA080X-12481
	
	
	200
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA050X-1489
	58 5/8"

(1489 mm)


	22.0 lb
(10.0 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODBA075X-1489
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA100X-14891
	
	
	200
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA060X-1710
	67 5/16"

(1710 mm)
	25.0 lb
(11.4 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA090X-1710
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA120X-17101
	
	
	200
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA070X-1947
	76 5/8"

(1947 mm)
	28.3 lb
(12.8 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA105X-1947
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA140X-19471
	
	
	200
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA080X-2170
	85 7/16"

(2170 mm)
	31.3 lb
(14.2 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA120X-2170
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA160X-21701
	
	
	200
	1600
	1600/1200
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA090X-2395
	94 5/16"

(2395 mm)
	34.4 lb
(15.6 kg)
	100
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA135X-2395
	
	
	150
	1350
	1350/1013
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODBA180X-23951
	
	
	200
	1800
	1800/1350
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODBA100X-2627
	103 7/16"

(2627 mm)
	37.6 lb
(17.6 kg)
	100
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODBA150X-2627
	
	
	150
	1500
	1500/1125
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODBA200X-26271
	
	
	200
	2000
	2000/1500
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODBA225X-26271
	
	
	200
	2250
	2250/1688
	-----
	-----
	(
	
	(
	
	(
	
	(
	


1 Not for residential use in the United States.
2 208V = 75% of wattage at 240V.
3 X = 2 (120V), 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
( = Available.

Add "BL" for white, "AM" for almond.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BAI
	Bottom fresh air inlet
	

	-
	BD
	Clean back
	

	KIT-ODBA-CE
	-
	Outside corner, 4 in. (102 mm)
	

	KIT-ODBA-CI
	-
	Inside corner, 4 in. (102 mm)
	

	KIT-ODBA-JT
	-
	Splice plate, 2 in. (51 mm)
	

	KIT-ODBA-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 2 in. (51 mm)
	

	KIT-ODBA-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-ODBA-PEC
	-
	Square-shaped pedestal kit (2), 2 in. (51 mm)
	

	ODBA-SV-XX
	-
	Empty cabinet length of XX mm (minimum: 154 mm, maximum: 2625 mm)
	

	Controls
	
	
	

	KIT-ODBA-DIS203
	DIS203
	Disconnect switch, 20A at 277V max.
	

	KIT-ODBA-DIS403
	DIS403
	Disconnect switch, 40A at 600V max.
	

	-
	HA
	Linear high-limit temperature control for high altitude (3000 ft. to 8200 ft.)
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-ODBA-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-ODBA-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-ODBA-RT-1201
	RT1
	Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V
	

	KIT-ODBA-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-ODBA-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-ODBA-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-ODBA-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-ODBA-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-ODBA-TB6
	TB6
	Single-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODBA-TB262
	TB262
	Double-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODBA-TB6-AV
	TB6AV
	Single-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODBA-TB26-AV2
	TB26AV2
	Double-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODBA-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A max. at 347V max.
	

	KIT-ODBA-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-ODBA-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 "Off" position.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


With bottom


fresh air inlet








180, 3e Avenue, L’Islet (Québec)  G0R 2C0  CANADA • Phone: 1 800 463-7043 • (418) 247-3947 • Fax: 1 800 662-7801 • (418) 247-7801 • www.ouellet.com • info@ouellet.com


