[image: image1.jpg]




Approval Drawings

Series

ODI
Aluminum Sloped Top Draft Barrier

[image: image5.jpg]@DUELLET



    [image: image2.emf]







[image: image3.jpg]




Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 



aluminum, semi-gloss black, sand.  


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.

Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.
Construction
-
14-gauge (0.0787 in. [2 mm]) aluminum front cover.


-
18-gauge satin coat steel cabinet.


-
Screw assembly for added strength.


-
Full length built-in wireway.


-
Pencil-proof openings less than 1/4 in. (6.4 mm).


-
Front fresh air inlet; top warm air outlet.



- Bottom fresh air inlet available (-BAI).

-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset. 
High altitude version available (-HA).


-
End caps included. 

Heating element
-
Stainless steel tubular heating element with aluminum ﬁns.

-
Floating heating element on high-temperature nylon bushings


reducing expansion noises.

Watt density
-
Average standard watt density of 275W/ft. 

-
Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control
-
Built-in thermostat available with a control knob 



or tamperproof.

· Mechanical, electronic or pneumatic relays available 


(installed on the right end only).

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Heater must be installed at least 2 in. (51 mm) from finished floor (for -BAI option).


-
Mounting holes spaced on 4 in. (102 mm) intervals for ease of installation.


-
Wall or floor mounted installation. 


-
Variety of accessories available for wall-to-wall installation.

-
Pedestal kit available.

Warranty
-
3-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center, private residence.

[image: image4.emf]








Average Standard Watt Density 275W/ft.1
	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	120V
	Qty
	208V
	Qty
	240/208V2
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	500
	500/375
	ODI0502
	
	ODI0508
	
	ODI0500
	
	ODI0507
	
	-
	-
	29 1/16
	738
	9.1
	4.1

	750
	750/563
	ODI0752
	
	ODI0758
	
	ODI0750
	
	ODI0757
	
	ODI0756
	
	39 1/16
	992
	11.9
	5.4

	1000
	1000/750
	ODI1002
	
	ODI1008
	
	ODI1000
	
	ODI1007
	
	ODI1006
	
	49 5/16
	1253
	14.7
	6.6

	1250
	1250/938
	ODI1252
	
	ODI1258
	
	ODI1250
	
	ODI1257
	
	ODI1256
	
	58 13/16
	1494
	17.3
	7.9

	1500
	1500/1125
	ODI1502
	
	ODI1508
	
	ODI1500
	
	ODI1507
	
	ODI1506
	
	67 1/2
	1715
	19.7
	9.0

	1750
	1750/1313
	-
	-
	ODI1758
	
	ODI1750
	
	ODI1757
	
	ODI1756
	
	76 7/8
	1952
	22.3
	10.1

	2000
	2000/1500
	-
	-
	ODI2008
	
	ODI2000
	
	ODI2007
	
	ODI2006
	
	85 5/8
	2175
	24.7
	11.2

	2250
	2250/1688
	-
	-
	ODI2258
	
	ODI2250
	
	ODI2257
	
	ODI2256
	
	94 1/2
	2400
	27.2
	12.3

	2500
	2500/1875
	-
	-
	ODI2508
	
	ODI2500
	
	ODI2507
	
	ODI2506
	
	103 5/8
	2632
	29.7
	13.5


Average Low Density Models

	Product #3
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V2
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty

	ODI020X-738
	29 1/16"

(738 mm)
	9.1 lb
(4.1 kg)
	100
	200
	200/150
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODI030X-7381
	
	
	150
	300
	300/225
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODI040X-7381
	
	
	200
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI030X-992
	39 1/16"

(992 mm)
	11.9 lb
(5.4 kg)
	100
	300
	300/225
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI045X-9921
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI060X-9921
	
	
	200
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI040X-1253
	49 5/16"

(1253 mm)
	14.7 lb
(6.6 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI060X-12531
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI080X-12531
	
	
	200
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI050X-1494
	58 13/16"

(1494 mm)


	17.3 lb
(7.9 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODI075X-14941
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI100X-14941
	
	
	200
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI060X-1715
	67 1/2"

(1715 mm)
	19.7 lb
(9.0 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI090X-17151
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI120X-17151
	
	
	200
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI070X-1952
	76 7/8"

(1952 mm)
	22.3 lb
(10.1 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI105X-19521
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI140X-19521
	
	
	200
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI080X-2175
	85 5/8"

(2175 mm)
	24.7 lb
(11.2 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI120X-21751
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI160X-21751
	
	
	200
	1600
	1600/1200
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODI090X-2400
	94 1/2"

(2400 mm)
	27.2 lb
(12.3 kg)
	100
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI135X-24001
	
	
	150
	1350
	1350/1013
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODI180X-24001
	
	
	200
	1800
	1800/1350
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODI100X-2632
	103 5/8"

(2632 mm)
	29.7 lb
(13.5 kg)
	100
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI150X-26321
	
	
	150
	1500
	1500/1125
	(
	
	(
	
	(
	
	(
	
	(
	

	ODI200X-26321
	
	
	200
	2000
	2000/1500
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODI225X-26321
	
	
	200
	2250
	2250/1688
	-----
	-----
	(
	
	(
	
	(
	
	(
	


1 Not for residential use in the United-States.

2 208V = 75% of wattage at 240V.
3 X = 2 (120V), 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
( = Available.

Add "BL" for white, "AM" for almond.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.
Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BAI
	Bottom fresh air inlet
	

	-
	BD1
	Clean back
	

	KIT-ODI-CE
	-
	Outside corner, 4 in. (102 mm)
	

	KIT-ODI-CI
	-
	Inside corner, 4 in. (102 mm)
	

	KIT-ODI-JT
	-
	Splice plate, 2 in. (51 mm)
	

	KIT-ODI-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 2 in. (51 mm)
	

	KIT-ODI-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-ODI-PEC
	-
	Square-shaped pedestal kit (2), 2 in. (51 mm)
	

	ODI-SV-XX
	-
	Empty cabinet with length of XX mm (minimum: 154 mm, maximum: 2632 mm)
	

	Controls
	
	
	

	KIT-ODI-DIS204
	DIS204
	Disconnect switch, 20A at 277V max.
	

	KIT-ODI-DIS404
	DIS404
	Disconnect switch, 40A at 600V max.
	

	-
	HA
	Linear high-limit temperature control for high altitude (3000 ft. to 8200 ft.)
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-ODI-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-ODI-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-ODI-RT-120
	RT
	Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V 
	

	KIT-ODI-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-ODI-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-ODI-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-ODI-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-ODI-RT-6002
	RT2
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-ODI-TB6
	TB6
	Single-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODI-TB263
	TB263
	Double-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODI-TB6-AV
	TB6AV
	Single-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODI-TB26-AV3
	TB26AV3
	Double-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODI-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-ODI-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-ODI-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 For anodized aluminum heaters, the clean back option will be fixed with visible rivets.

2 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

3 "Off" position.

4 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


With bottom


fresh air inlet








180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

