[image: image1.jpg]




Approval Drawings

Series

ODIA
Steel Sloped Top Draft Barrier

[image: image5.jpg]@DUELLET



   [image: image2.emf]







[image: image3.jpg]




Features

Color
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 



aluminum, semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.

Construction
-
16-gauge steel front cover.


-
18-gauge satin coat steel cabinet.


-
Screw assembly for added strength.


-
Full length built-in wireway.


-
Front fresh air inlet; top warm air outlet.



- Bottom fresh air inlet available (-BAI).

-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset. 
High altitude version available (-HA).


-
End caps included. 

Heating element
-
Stainless steel tubular heating element with aluminum ﬁns.

-
Floating heating element on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 275W/ft.


-
Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control
-
Built-in thermostat available with a control knob 



or tamperproof.

· Mechanical, electronic or pneumatic relays available 


(installed on the right end only).

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Heater must be installed at least 2 in. (51 mm) from finished floor 



(for -BAI option).


-

Mounting holes spaced on 4 in. (102 mm) intervals for ease of installation.


-
Wall or floor mounted installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit available.

Warranty
-
1-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center, private residence.
[image: image4.emf]








Average Standard Watt Density Models 275W/ft.1
	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	277V
	Qty
	480V
	Qty
	in.
	mm
	lb
	kg

	500
	500/375
	ODIA0502
	
	ODIA0508
	
	ODIA0500
	
	ODIA0577
	
	-
	-
	28 7/8
	733
	11.6
	5.3

	750
	750/563
	ODIA0752
	
	ODIA0758
	
	ODIA0750
	
	ODIA0777
	
	ODIA0754
	
	38 7/8
	987
	15.1
	6.9

	1000
	1000/750
	ODIA1002
	
	ODIA1008
	
	ODIA1000
	
	ODIA1077
	
	ODIA1004
	
	49 1/8
	1248
	18.7
	8.5

	1250
	1250/938
	ODIA1252
	
	ODIA1258
	
	ODIA1250
	
	ODIA1277
	
	ODIA1254
	
	58 5/8
	1489
	22.0
	10.0

	1500
	1500/1125
	ODIA1502
	
	ODIA1508
	
	ODIA1500
	
	ODIA1577
	
	ODIA1504
	
	67 5/16
	1710
	25.0
	11.4

	1750
	1750/1313
	-
	-
	ODIA1758
	
	ODIA1750
	
	ODIA1777
	
	ODIA1754
	
	76 5/8
	1947
	28.3
	12.8

	2000
	2000/1500
	-
	-
	ODIA2008
	
	ODIA2000
	
	ODIA2077
	
	ODIA2004
	
	85 7/16
	2170
	31.3
	14.2

	2250
	2250/1688
	-
	-
	ODIA2258
	
	ODIA2250
	
	ODIA2277
	
	ODIA2254
	
	94 5/16
	2395
	34.4
	15.6

	2500
	2500/1875
	-
	-
	ODIA2508
	
	ODIA2500
	
	ODIA2577
	
	ODIA2504
	
	103 7/16
	2627
	37.6
	17.1


Average Low Watt Density Models

	Product #3
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V2
	120V
	Qty
	208V
	Qty
	240/208V
	Qty
	277V
	Qty
	480V
	Qty

	ODIA020X-733
	28 7/8"

(733 mm)
	11.6 lb
(5.3 kg)
	100
	200
	200/150
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODIA030X-733
	
	
	150
	300
	300/225
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	ODIA040X-7331
	
	
	200
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA030X-987
	38 7/8"

(987 mm)
	15.1 lb
(6.9 kg)
	100
	300
	300/225
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA045X-987
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA060X-9871
	
	
	200
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA040X-1248
	49 1/8"

(1248 mm)
	18.7 lb
(8.5 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA060X-1248
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA080X-12481
	
	
	200
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA050X-1489
	58 5/8"

(1489 mm)


	22.0 lb
(10.0 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	
	-----
	-----

	ODIA075X-1489
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA100X-14891
	
	
	200
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA060X-1710
	67 5/16"

(1710 mm)
	25.0 lb
(11.4 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA090X-1710
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA120X-17101
	
	
	200
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA070X-1947
	76 5/8"

(1947 mm)
	28.3 lb
(12.8 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA105X-1947
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA140X-19471
	
	
	200
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA080X-2170
	85 7/16"

(2170 mm)
	31.3 lb
(14.2 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA120X-2170
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA160X-21701
	
	
	200
	1600
	1600/1200
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODIA090X-2395
	94 5/16"

(2395 mm)
	34.4 lb
(15.6 kg)
	100
	900
	900/675
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA135X-2395
	
	
	150
	1350
	1350/1013
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODIA180X-23951
	
	
	200
	1800
	1800/1350
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODIA100X-2627
	103 7/16"

(2627 mm)
	37.6 lb
(17.6 kg)
	100
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	
	(
	

	ODIA150X-2627
	
	
	150
	1500
	1500/1125
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODIA200X-26271
	
	
	200
	2000
	2000/1500
	-----
	-----
	(
	
	(
	
	(
	
	(
	

	ODIA225X-26271
	
	
	200
	2250
	2250/1688
	-----
	-----
	(
	
	(
	
	(
	
	(
	


1 Not for residential use in the United States.

2 208V = 75% of wattage at 240V.

3 X = 2 (120V), 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
( = Available.

Add "BL" for white, "AM" for almond. Optional colors shown in the color chart section are available upon request.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.
Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BAI
	Bottom fresh air inlet
	

	-
	BD
	Clean back
	

	KIT-ODIA-CE
	-
	Outside corner, 4 in. (102 mm)
	

	KIT-ODIA-CI
	-
	Inside corner, 4 in. (102 mm)
	

	KIT-ODIA-JT
	-
	Splice plate, 2 in. (51 mm)
	

	KIT-ODIA-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 2 in. (51 mm)
	

	KIT-ODIA-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-ODIA-PEC
	-
	Square-shaped pedestal kit (2), 2 in. (51 mm)
	

	ODIA-SV-XX
	-
	Empty cabinet length of XX mm (minimum: 154 mm, maximum: 2625 mm)
	

	Controls
	
	
	

	KIT-ODIA-DIS203
	DIS203
	Disconnect switch, 20A at 277V max.
	

	KIT-ODIA-DIS403
	DIS403
	Disconnect switch, 40A at 600V max.
	

	-
	HA
	Linear high limit temperature control for high altitude (3000 ft. to 8200 ft.)
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-ODIA-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-ODIA-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-ODIA-RT-120
	RT
	Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V
	

	KIT-ODIA-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-ODIA-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-ODIA-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-ODIA-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-ODIA-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-ODIA-TB6
	TB6
	Single-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODIA-TB262
	TB262
	Double-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODIA-TB6-AV
	TB6AV
	Single-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODIA-TB26-AV2
	TB26AV2
	Double-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-ODIA-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-ODIA-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-ODIA-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 "Off" position.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date :
	

	Contact in Ouellet:
	

	Comments:


With bottom


fresh air inlet








180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

