[image: image1.jpg]27
20

\\\\\\\\

/////////////




[image: image3.jpg]@DUELLET



[image: image3.jpg]

Approval Drawings

disSeries

ODS
Ceiling Fan Heater
[image: image4.jpg]VERSION AVAILABLE




[image: image5.jpg]


 


Features

Color
-
Standard: white, almond.

· Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 


aluminum, semi-gloss black. 

· Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or-3 phase.

Construction
-
Outlet grille made of flat ribbon wire.


-
High-limit temperature control with automatic reset.
Fan
-
Totally enclosed and lifetime-lubricated ball bearing motor.


-
Fan delay purges heater of residual heat.

Heating element
-
Three stainless steel tubular heating elements with aluminum fins.

Control
-
240/208V control circuit standard (except for 2 to 5kW at 277V have 



277V control standard).

-
Built-in 240V contactor for some models (see table).


-
24V and 120V control circuit available.


-
Built-in tamperproof thermostat available. 


-
24V relay (with or without transformer) available.


-
Continuous circulation controlled by a built-in switch with power-on indicator 



light available (-CV).


Any remote thermostat or relay must be connected to the heater control terminal block.
Installation
-
Recommended height: between 8 ft. (2.4 m) and 12 ft. (3.6 m).


-
Recessed into insulated or T-bar ceiling (ODSR).


-
Surface mounting (ODSA and ODSB), T-BAR adaptor optional.


Note: We recommend installing this product on an outside ceiling to avoid vibrations spreading 


to an adjacent room.
Warranty
-
5-year warranty against defects.

Application
-
Apartment building, commercial building, drop ceiling, stairwell, garage.

[image: image2.emf]








Models

	Watts
	Volts (ph)
	Product #
	Qty
	Volts (ph)
	Product #
	Qty
	cfm
	Temperature Rise
	Motor

	
	
	
	
	
	
	
	
	°C
	°F
	HP
	rpm

	ODSA Surface

	2000
	240 (1)
	ODSAU02000
	
	240 (3)
	ODSAU020301
	
	310
	11
	20
	1/50
	1550

	3000
	240 (1)
	ODSAU03000
	
	240 (3)
	ODSAU030301
	
	310
	17
	30
	1/50
	1550

	4000
	240 (1)
	ODSAU04000
	
	240 (3)
	ODSAU040301
	
	310
	23
	41
	1/50
	1550

	5000
	240 (1)
	ODSAU050001
	
	240 (3)
	ODSAU050301
	
	310
	28
	51
	1/50
	1550

	2000
	208 (1)
	ODSAU02008
	
	208 (3)
	ODSAU020381
	
	310
	11
	20
	1/50
	1550

	3000
	208 (1)
	ODSAU03008
	
	208 (3)
	ODSAU030381
	
	310
	17
	30
	1/50
	1550

	4000
	208 (1)
	ODSAU04008
	
	208 (3)
	ODSAU040381
	
	310
	23
	41
	1/50
	1550

	5000
	208 (1)
	ODSAU050081
	
	208 (3)
	ODSAU050381
	
	310
	28
	51
	1/50
	1550

	2000
	277 (1)
	ODSAU02077
	
	-
	-
	
	310
	11
	20
	1/50
	1550

	3000
	277 (1)
	ODSAU03077
	
	-
	-
	
	310
	17
	30
	1/50
	1550

	4000
	277 (1)
	ODSAU04077
	
	-
	-
	
	310
	23
	41
	1/50
	1550

	5000
	277 (1)
	ODSAU05077
	
	-
	-
	
	310
	28
	51
	1/50
	1550

	2000
	480 (1)
	ODSAU020041
	
	480 (3)
	ODSAU020341
	
	310
	11
	20
	1/50
	1550

	3000
	480 (1)
	ODSAU030041
	
	480 (3)
	ODSAU030341
	
	310
	17
	30
	1/50
	1550

	4000
	480 (1)
	ODSAU040041
	
	480 (3)
	ODSAU040341
	
	310
	23
	41
	1/50
	1550

	5000
	480 (1)
	ODSAU050041
	
	480 (3)
	ODSAU050341
	
	310
	28
	51
	1/50
	1550

	ODSB Surface

	7500
	240 (1)
	ODSBU075001
	
	240 (3)
	ODSBU075301
	
	600
	22
	39
	1/33
	1550

	10000
	240 (1)
	ODSBU100001
	
	240 (3)
	ODSBU100301
	
	600
	29
	53
	1/33
	1550

	7500
	208 (1)
	ODSBU075081
	
	208 (3)
	ODSBU075381
	
	600
	22
	39
	1/33
	1550

	9900
	208 (1)
	ODSBU099081
	
	208 (3)
	ODSBU099381
	
	600
	29
	53
	1/33
	1550

	7500
	277 (1)
	ODSBU075771
	
	347 (1)
	-
	
	600
	22
	39
	1/33
	1550

	10000
	277 (1)
	ODSBU100771
	
	347 (1)
	-
	
	600
	29
	53
	1/33
	1550

	7500
	480 (1)
	ODSBU075041
	
	480 (3)
	ODSBU075341
	
	600
	22
	39
	1/33
	1550

	10000
	480 (1)
	ODSBU100041
	
	480 (3)
	ODSBU100341
	
	600
	29
	53
	1/33
	1550

	ODSR Recessed

	2000
	240 (1)
	ODSRU02000
	
	240 (3)
	ODSRU020301
	
	310
	11
	20
	1/50
	1550

	3000
	240 (1)
	ODSRU03000
	
	240 (3)
	ODSRU030301
	
	310
	17
	39
	1/50
	1550

	4000
	240 (1)
	ODSRU04000
	
	240 (3)
	ODSRU040301
	
	310
	23
	41
	1/50
	1550

	5000
	240 (1)
	ODSRU050001
	
	240 (3)
	ODSRU050301
	
	310
	28
	51
	1/50
	1550

	2000
	208 (1)
	ODSRU02008
	
	208 (3)
	ODSRU020381
	
	310
	11
	20
	1/50
	1550

	3000
	208 (1)
	ODSRU03008
	
	208 (3)
	ODSRU030381
	
	310
	17
	30
	1/50
	1550

	4000
	208 (1)
	ODSRU04008
	
	208 (3)
	ODSRU040381
	
	310
	23
	41
	1/50
	1550

	5000
	208 (1)
	ODSRU050081
	
	208 (3)
	ODSRU050381
	
	310
	28
	51
	1/50
	1550

	2000
	277 (1)
	ODSRU02077
	
	-
	-
	
	310
	11
	20
	1/50
	1550

	3000
	277 (1)
	ODSRU03077
	
	-
	-
	
	310
	17
	30
	1/50
	1550

	4000
	277 (1)
	ODSRU04077
	
	-
	-
	
	310
	23
	41
	1/50
	1550

	5000
	277 (1)
	ODSRU05077
	
	-
	-
	
	310
	28
	51
	1/50
	1550

	2000
	480 (1)
	ODSRU020041
	
	480 (3)
	ODSRU020341
	
	310
	11
	20
	1/50
	1550

	3000
	480 (1)
	ODSRU030041
	
	480 (3)
	ODSRU030341
	
	310
	17
	30
	1/50
	1550

	4000
	480 (1)
	ODSRU040041
	
	480 (3)
	ODSRU040341
	
	310
	23
	41
	1/50
	1550

	5000
	480 (1)
	ODSRU050041
	
	480 (3)
	ODSRU050341
	
	310
	28
	51
	1/50
	1550


1 Built-in 240V contactor.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	-
	120
	120V control circuit
	

	-
	CV
	Summer fan switch and pilot light
	

	KIT-ODS-DIS202
	DIS202
	Disconnect switch, double-pole, 20A at 277V and less (80% = 16A)
	

	KIT-ODS-DIS402
	DIS402
	Disconnect switch, triple-pole, 40A at 600V max. (80% = 32A)
	

	-
	DIS802
	Disconnect switch, triple-pole, 80A at 600V (80% = 64A)
	

	KIT-ODS-R
	R
	24V control relay, without transformer
	

	-
	RCV24
	Summer fan relay 24V, remote control and pilot light (switch not included)
	

	-
	RCV240
	Summer fan relay 240V, remote control and pilot light (switch not included)
	

	-
	RT
	24V control relay, with transformer
	

	KIT-ODS-T-AV
	TAV
	Thermostat tamperproof
	

	KIT-ODSA-T-BAR
	-
	Adaptor for T-bar ceiling, ODSA only
	

	KIT-ODSB-T-BAR
	-
	Adaptor for T-bar ceiling, ODSB only
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

2 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments: 


180, 3e Avenue, L’Islet (Québec)  G0R 2C0  CANADA • Phone: 1 800 463-7043 • (418) 247-3947 • Fax: 1 800 662-7801 • (418) 247-7801 • www.ouellet.com • info@ouellet.com


