[image: image1.jpg]




Approval Drawings

Series

OHB
High Density Aluminum Draft Barrier

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal,  



aluminum, semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.

Voltage
-
208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.
Construction
-
14-gauge (0.0787 in. [2 mm]) aluminum front cover.


-
18-gauge satin coat steel cabinet.


-
Screw assembly for added strength.


-
Full length built-in wireway.


-
Separate low voltage wireway (-WW) available.


-
Pencil-proof openings less than 1/4 in. (6.4 mm).


-
Bottom fresh air inlet, top warm air outlet.


-
Clean back available (-BD).

· Linear high-limit temperature control with automatic reset. 


High altitude version available (-HA).


-
End caps included.

Heating element
-
Two stainless steel tubular heating elements with aluminum fins.

-
Floating heating elements on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density 355W/ft.
· Average low watt density 175W/ft, 250W/ft.

· Average high watt density 500W/ft.
Control
-
Built-in thermostat available with a control knob or tamperproof.
· Mechanical, electronic or pneumatic relays available. 

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Not for residential use in the United States.


-
Heater must be installed at least 3 in. (76 mm) from ﬁnished ﬂoor.


-
Mounting holes spaced on 2 in. (51 mm) intervals for ease of installation.


-
Installation on wall or ﬂoor mounted with pedestals.


-
Pedestal kit available.

-
Variety of accessories available for wall-to-wall installation.

Warranty
-
3-year warranty against defects.

Applications
-
Commercial building, office building, hospital, daycare center, private residence.

[image: image3.jpg]r———f147mm

Side View

53/4"

Front View

147 mm

53/4"

73 mm -
27/8"

Bottom View

KOE @6.4 mm 60 mm

\ KOE @1/4" 23/8"
AN
T o T = \ [
o o o o o ° 153 mm

AT

KOE @22 mm =47 mm
KOE @7/8" 17/8"

Clean Back (-BD) Standard Finish | 575 mm
on the Back of the Heater 21/4"

Rear View




Average Standard Watt Density Models 355W/ft. 
	Watts
	Watts
	Product #
	Length
	Weight

	
	240/208V1
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	750
	750/563
	OHB0758
	
	OHB0750
	
	OHB0757
	
	-
	-
	23 5/8
	600
	10.7
	4.8

	1000
	1000/750
	OHB1008
	
	OHB1000
	
	OHB1007
	
	-
	-
	35 7/16
	900
	14.1
	6.4

	1400
	1400/1050
	OHB1408
	
	OHB1400
	
	OHB1407
	
	OHB1406
	
	47 1/4
	1200
	17.6
	8.0

	1750
	1750/1313
	OHB1758
	
	OHB1750
	
	OHB1757
	
	OHB1756
	
	59 1/16
	1500
	21.1
	9.6

	2100
	2100/1577
	OHB2108
	
	OHB2100
	
	OHB2107
	
	OHB2106
	
	70 7/8
	1800
	24.6
	11.1

	2450
	2450/1840
	OHB2458
	
	OHB2450
	
	OHB2457
	
	OHB2456
	
	82 11/16
	2100
	28.0
	12.7

	2800
	2800/2103
	OHB2808
	
	OHB2800
	
	OHB2807
	
	OHB2806
	
	94 1/2
	2400
	31.5
	14.3


Average Low Watt Density Models

	Product #2
	Length
	Weight
	Average Density W/ft.
	Watts
	Watts

240/208V1
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty

	OHB037X-600
	23 5/8"

(600 mm)
	10.7 lb
(4.8 kg)
	175
	375
	375/281
	(
	
	(
	
	-
	-
	-
	-

	OHB050X-600
	
	
	250
	500
	500/375
	(
	
	(
	
	-
	-
	-
	-

	OHB050X-900
	35 7/16"

(900 mm)
	14.1 lb
(6.4 kg)
	175
	500
	500/375
	(
	
	(
	
	(
	
	-
	-

	OHB075X-900
	
	
	250
	750
	750/563
	(
	
	(
	
	(
	
	-
	-

	OHB070X-1200
	47 1/4"

(1200 mm)
	17.6 lb
(8.0 kg)
	175
	700
	700/525
	(
	
	(
	
	(
	
	(
	

	OHB100X-1200
	
	
	250
	1000
	1000/750
	(
	
	(
	
	(
	
	(
	

	OHB087X-1500
	59 1/16"

(1500 mm)
	21.1 lb
(9.6 kg)
	175
	875
	875/656
	(
	
	(
	
	(
	
	(
	

	OHB125X-1500
	
	
	250
	1250
	1250/938
	(
	
	(
	
	(
	
	(
	

	OHB105X-1800
	70 7/8"

(1800 mm)
	24.6 lb
(11.1 kg)
	175
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	

	OHB150X-1800
	
	
	250
	1500
	1500/1125
	(
	
	(
	
	(
	
	(
	

	OHB122X-2100
	82 11/16"

(2100 mm)
	28.0 lb
(12.7 kg)
	175
	1225
	1225/919
	(
	
	(
	
	(
	
	(
	

	OHB175X-2100
	
	
	250
	1750
	1750/1313
	(
	
	(
	
	(
	
	(
	

	OHB140X-2400
	94 1/2"

(2400 mm)
	31.5 lb
(14.3 kg)
	175
	1400
	1400/1050
	(
	
	(
	
	(
	
	(
	

	OHB200X-2400
	
	
	250
	2000
	2000/1500
	(
	
	(
	
	(
	
	(
	


Average High Watt Density Models 500W/ft. 
	Watts
	Watts

240/208V1
	Product #
	Length
	Weight

	
	
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	1000
	1000/750
	OHBH1008
	
	OHBH1000
	
	OHBH1007
	
	OHBH1006
	
	23 5/8
	600
	10.7
	4.8

	1500
	1500/1125
	OHBH1508
	
	OHBH1500
	
	OHBH1507
	
	OHBH1506
	
	35 7/16
	900
	14.1
	6.4

	2000
	2000/1500
	OHBH2008
	
	OHBH2000
	
	OHBH2007
	
	OHBH2006
	
	47 1/4
	1200
	17.6
	8.0

	2500
	2500/1875
	OHBH2508
	
	OHBH2500
	
	OHBH2507
	
	OHBH2506
	
	59 1/16
	1500
	21.1
	9.6

	3000
	3000/2250
	OHBH3008
	
	OHBH3000
	
	OHBH3007
	
	OHBH3006
	
	70 7/8
	1800
	24.6
	11.1

	3500
	3500/2625
	OHBH35083
	
	OHBH3500
	
	OHBH3507
	
	OHBH3506
	
	82 11/16
	2100
	28.0
	12.7

	4000
	4000/3000
	OHBH40083
	
	OHBH40003
	
	OHBH4007
	
	OHBH4006
	
	94 1/2
	2400
	31.5
	14.3


1 208V = 75% of wattage at 240V.
2 X = 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
3 If the control option "24V electronic relay" is required, these products need two electronic relays.
( = Available.

Add "BL" for white, "AM" for almond.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.
Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD1
	Clean back
	

	KIT-OHB-CE
	-
	Outside corner, 8 in. (203 mm)
	

	KIT-OHB-CI
	-
	Inside corner, 8 in. (203 mm)
	

	KIT-OHB-JT
	-
	Splice plate, 2 in. (51 mm)
	

	KIT-OHB-JT-PE
	-
	Contour splice plate for BD option and/or heater with pedestals, 2 in. (51 mm)
	

	KIT-OHB-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	OHB-SV-XX
	-
	Empty cabinet with length of XX mm (minimum: 154 mm, maximum: 2400 mm)
	

	Controls
	
	
	

	KIT-OHB-DIS203
	DIS203
	Disconnect switch, 20A at 277V max.
	

	KIT-OHB-DIS403
	DIS403
	Disconnect switch, 40A at 600V max.
	

	-
	HA
	Linear high-limit temperature control for high altitude (3000 ft. to 8200 ft.)
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-OHB-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OHB-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-OHB-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-OHB-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-OHB-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-OHB-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-OHB-RT-6002
	RT2
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-OHB-T
	T
	Single-pole thermostat: 25A at 208V, 240V - 10A at 277V, 347V, 480V, 600V
	

	KIT-OHB-T24
	T24
	Double-pole thermostat: 30A at 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OHB-T-AV
	TAV
	Single-pole tamperproof thermostat: 25A at 208V, 240V - 10A at 277V, 347V, 480V, 600V
	

	KIT-OHB-T2-AV4
	T2AV4
	Double-pole tamperproof thermostat: 30A at 208V, 240V - 15A at 277V, 347V, 600V
	

	KIT-OHB-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-OHB-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-OHB-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	-
	WW
	24V wireway includes high temperature wiring
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 For anodized aluminum heaters, the clean back option will be fixed with visible rivets. 

2  These 2-wire relays with transformer can't supply a 3-wire low voltage thermostats.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
4 "Off" position.
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

