[image: image5.jpg]@DUELLET



[image: image5.jpg]

Approval Drawings

Series

OHX
Explosion-Proof Unit Heater

[image: image1.emf]







   [image: image2.jpg]




Features

Color
-
Standard: red. 

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 480V, 600V, 1 or 3-phase.

Construction
-
14-gauge steel cabinet.

· Adjustable anodized aluminum louvers.

· Cast aluminum control and element enclosure lids NEMA Type 7 and 9 with O-ring.
· Fan Guard: multiple horizontal and vertical stiffening wires.

Protection
-
Stainless steel high temperature pressure relief device.

· Two high-limit temperature controls: one with automatic


reset and one with manual reset.
Fan
-
Explosion-proof, thermally protected, permanently lubricated ball bearing motor.


-
3 to 20kW: 1/4 HP, 1725 rpm.


-
25 to 35kW: 1/2 HP, 1725 rpm.

Heat exchanger
-
High grade metal-sheathed elements ﬁns with ethylene glycol/water solution.


-
Long-life, low watt density.


-
Evacuated and sealed, carbon steel tube core with 10 aluminum ﬁns per inch.

Temperature code
-
Division System: 5 to 30kW = T3B 165 °C (329 °F), 3kW/35kW = T3A 180 °C 


(356 °F).

-
Zone System T3 200 °C (392 °F).

Control
-
120VAC control (standard).


-
Optional 24VAC control (recommended due to safer voltage). Required for use with 

electronic thermostat.

-
Optional built-in or wall thermostat (bi-metal or electronic).

-
Optional built-in or wall disconnect switch.
Additional Options
-
Pilot light.
· Continuous fan.
· Heresite coatings.
Installation


        - Accessories available.
Warranty
-
3-year warranty against defects.

Application
-
Paint storage area, petrochemical plant, reﬁnery, chemical plant, mining industry, sawmill.
Consult the Electrical Code in your area before installing this unit.
[image: image3.jpg]168 mm

65/8"
137 mm 6 mm
53/8" 1/4"
Front View 6mm
1/4"
Optional built-in
disconnect switch 279 mm
11" Louvers
36 mm max.

13/8” max.

Optional
explosion-proof

built-in thermostat Side View

1"NPT
Main electrical entry
for disconnect option

1"NPT
Main electrical entry
no disconnect fitted

4 X @9/16" (14 mm)
Mounting holes

L57 mm
21/4"
\ 3/4" NPT,
External thermostat
entry
214 mm 5”7 86 mm
87/16" 33/8"
Top View

Models |3 to 10kW |15 to 20kW |25 to 35kW
Fan 12" 16" 20”
305mm |406.4mm | 508 mm
. in. in. in.
Dim. (mm) (mm) (mm)
A 7.5 7.5 7.5
(191) (191) (191
B 18.2 223 26.3
(462) (566) (668
c 16.3 20.3 243
(414) (516) (617)
D 19.0 23.0 27.0
(483) (584) (686,
E 19.5 235 275
(495) (597) (699)
F 3.1 5.1 7.1
(79) (130) (180,
G 223 223 233
(566) (566) (592





[image: image4.emf]








Models

	kW
	BTU/hr
	Product #
	cfm
	T° Rise
	T° Code2
	Weight1

	
	
	208V
(1 ph)
	Qty
	208V
(3 ph)
	Qty
	240V
(1 ph)
	Qty
	240V
(3 ph)
	Qty
	480V
(3 ph)
	Qty
	600V
(3 ph)
	Qty
	
	oC
	oF
	
	lb
	kg

	 3.0
	10236
	OHX03008
	
	OHX03038
	
	OHX03000
	
	OHX03030
	
	OHX03034
	
	OHX03036
	
	350
	18.0
	32.2
	T3A
	188
	85.3

	 5.0
	17060
	OHX05008
	
	OHX05038
	
	OHX05000
	
	OHX05030
	
	OHX05034
	
	OHX05036
	
	400
	24.5
	44.0
	T3B
	188
	85.3

	7.5
	25590
	OHX07508
	
	OHX07538
	
	OHX07500
	
	OHX07530
	
	OHX07534
	
	OHX07536
	
	600
	23.7
	42.5
	T3B
	188
	85.3

	10.0
	34120
	-
	-
	OHX10038
	
	OHX10000
	
	OHX10030
	
	OHX10034
	
	OHX10036
	
	800
	23.2
	41.8
	T3B
	192
	87.1

	15.0
	51180
	-
	-
	OHX15038
	
	-
	-
	OHX15030
	
	OHX15034
	
	OHX15036
	
	1200
	22.6
	40.6
	T3B
	224
	101.6

	20.0
	68240
	-
	-
	-
	-
	-
	-
	-
	-
	OHX20034
	
	OHX20036
	
	1700
	21.1
	38.0
	T3B
	224
	101.6

	25.0
	85300
	-
	-
	-
	-
	-
	-
	-
	-
	OHX25034
	
	OHX25036
	
	2100
	21.8
	39.1
	T3B
	261
	118.4

	30.0
	102360
	-
	-
	-
	-
	-
	-
	-
	-
	OHX30034
	
	OHX30036
	
	3000
	18.2
	32.6
	T3B
	261
	118.4

	35.0
	119420
	-
	-
	-
	-
	-
	-
	-
	-
	OHX35034
	
	OHX35036
	
	3000
	20.1
	37.9
	T3A
	261
	118.4


Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	
	Ouellet
	Reference
	
	

	-
	24
	B
	Transformer and contactor for 24VAC (required for use with built-in or wall mount electronic thermostat)
	

	-
	DIS
	D
	Built-in disconnect switch
	

	-
	T1
	-
	Explosion-proof built-in bi-metal thermostat, range 5 °C (40 °F) to 25 °C (80 °F)
	

	-
	T23
	-
	Explosion-proof, electronic thermostat (low voltage), 5 °C (40 °F) to 25 °C (80 °F) (suitable for 24 volt control circuit only)
	

	-
	L
	P
	Pilot light “heat on” 
	

	-
	FC
	F
	Continuous fan operation
	

	OUE-BTX2-15A-W-N-A
	-
	-
	Explosion-proof, wall mount bi-metal thermostat, 5 °C (40 °F) to 25 °C (80 °F) (suitable for 24VAC or 120VAC control circuit)
	

	OUE-XET1-1-W-N-A3
	-
	-
	Explosion-proof, electronic wall mount thermostat (low voltage), 5 °C (40 °F) to 25 °C (80 °F), (suitable for 24 volt control circuit only)
	

	OUE-BLK1-W-N-A
	-
	-
	Thermostat conversion kit allowing interchangeability from built-in thermostat to wall mount configuration 
	

	OUE-XDC-01
	-
	-
	Explosion-proof wall mount disconnect switch, 600V, 50A max
	

	OHX-MS
	-
	-
	Hanging mounting bracket, all models. Ideal and economical if adequate overhead structure exists. Requires 1/2 in. (12.5 mm) pipe, cut and threaded (min. Sch. 40) not supplied.
	

	OHX-MBX4
	-
	-
	Basic mounting bracket. Can be bolted or welded directly to structural steel or concrete.
	

	OHX-MMX4
	-
	-
	Wall mounting bracket. Use in buildings that have substantial walls. The Z sections provide additional support where necessary.
	

	OHX-MTX4
	-
	-
	Pipe mounting bracket. For buildings with insufficient strength to use other types of mounting brackets. Requires 3 in. (75 mm) pipe (3 1/2 in. [87.5 mm] O.D., min. Sch. 40) not supplied.
	

	-
	HCCX4, 5
	H1
	Heresite P-413 baked phenolic coating of heat exchanger core only
	

	-
	HCBX4, 5
	H2
	Heresite P-413 baked phenolic coating of louvers, fan blade, fan guard & cabinet parts
	

	-
	HCUX4, 5
	H3
	Heresite P-413 baked phenolic coating of heat exchanger core, louvers, fan blade, 
fan guard & cabinet parts
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 
1 Shipping weight
2 Temperature code: T3B = 165 °C (329 °F), T3A = 180 °C (356 °F).
3 Built-in transformer and contactor for 24VAC are required, add « -24 » to the product number.

4 X= 1 (3 to 10kW units), 2 (15 to 20kW units), 3 (25 to 35kW units).
5 We do not Heresite coat the explosion-proof motor, control enclosure, aluminium conduit or any options such as disconnect or integral thermostat.

 Allow additional 4 to 6 weeks lead time.
Standard color is red.
ATEX, IECEx and UKEX approved models available upon request, please contact our customer service.
Approved locations
Class I, Divisions 1 and 2, Groups C and D.

Class II, Divisions 1 and 2, Groups F and G.

Temperature code: T3B (5 to 30kW), T3A (3kW/35kW).
Class I, Zones 1 & 2, Groups IIA & IIB, T3.
Temperature limitations
Ambient temperature: -40 °C to 40 °C (-40 °F to 104 °F).
Maximum altitude: 3048 m (10000 ft.) above sea level.
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

