[image: image1.jpg]




Approval Drawings

Series

OLA
High Density Architectural Cabinet Convector

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 

· Optional (upcharge available): metallic silver, bronze, metallic charcoal,


aluminum, semi-gloss black, sand.

· Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
20-gauge steel cabinet.


-
16-gauge steel front cover.

-
Extruded aluminum bar grilles prevent insertion of foreign objects.


-
Front fresh air inlet; top warm air outlet.



- Front warm air outlet available (-FR).

-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset.

Heating element
-
Three stainless steel tubular heating elements with aluminum ﬁns.

-
Floating heating elements on high-temperature bushings, 


reducing expansion noises.

Watt density
-
Average standard watt density of 1000W/ft.

-
Average low watt density of 500W/ft., 750W/ft.

Control
-
Built-in tamperproof thermostat available.

· Mechanical, electronic or pneumatic relays available.

Note: Single-pole thermostat is for 1 phase model only.

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Not for residential use in the United States.


-
Wall or ﬂoor mounted installation.

-
Front outlet -FR models may be recessed.


-
Mounting holes spaced on 2 in. (51 mm) intervals for ease of installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit or sub-base available.

Warranty
-
3-year warranty against defects.

Application
-
Commercial building, hospital, daycare center.
[image: image3.jpg]KOE @6.4 mm
KOE @1/4"

KOE @22 mm
KOE @7/8"

317 mm
12172"

&

L]

215mm
81/2"

Right Side View

184 mm

204 mm

71/4"

Unit with Front Grilles (-FR)
Recessed

KOE 102 x 52 mm

‘ ~KOE4"x 2"

512mm
F 203/16"
L]
Y
i
76 mm ~—KOE @28-@22 mm
3" KOE @1 1/8"-@7/8 Front View

Unit with Grille on Top
Not Recessed

KOE @6.4 mm

58 mm
21/4"

KOE @1/4" T r

P KOE @28-@22 mm
KOE @1 1/8"-@7/8"

Bottom View

132mm
53/16"




Average Standard Watt Density Models 1000W/ft. 

	Watts
	Watts

240/208V1
	Product #
	Length
	Weight

	
	
	208V
(1 ph)
	Qty
	208V
(3 ph)
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
(1 ph)
	Qty
	600V
(3 ph)
	Qty
	in.
	mm
	lb
	kg

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	2000
	2000/1500
	OLA2008
	
	OLA20382
	
	OLA2000
	
	OLA2007
	
	OLA2006
	
	OLA20362
	
	27 3/16
	690
	37.0
	16.8

	3000
	3000/2250
	OLA3008
	
	OLA30382
	
	OLA3000
	
	OLA3007
	
	OLA3006
	
	OLA30362
	
	37 3/16
	944
	47.0
	21.3

	4000
	4000/3000
	OLA40082
	
	OLA40382
	
	OLA40002
	
	OLA4007
	
	OLA40062
	
	OLA40362
	
	47 3/16
	1198
	57.0
	25.9

	5000
	5000/3750
	OLA50083
	
	OLA50382
	
	OLA50002
	
	OLA5007
	
	OLA50062
	
	OLA50362
	
	57 3/16
	1452
	67.0
	30.4

	6000
	6000/4500
	OLA60083
	
	OLA60383
	
	OLA60003
	
	OLA60072
	
	OLA60063
	
	OLA60362
	
	65 3/16
	1655
	79.0
	35.8


Average Low Watt Density Models

	Product #4
	Length
	Weight
	AverageDensity W/ft.
	Watts
	208V
(1 ph)
	Qty
	208V
(3 ph)
	Qty
	240V
	Qty
	347V
	Qty
	600V

(1 ph)
	Qty
	600V 

(3 ph)
	Qty

	OLA10XX-690
	27 3/16"
(690 mm)
	37.0 lb
(16.8 kg)
	500
	1000
	(
	
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OLA15XX-690
	
	
	750
	1500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA15XX-944
	37 3/16"
(944 mm)
	47.0 lb
(21.3 kg)
	500
	1500
	(
	
	(
	
	(
	
	(
	
	-----
	-----
	(
	

	OLA22XX-944
	
	
	750
	2250
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA20XX-1198
	47 3/16"
(1198 mm)
	57.0 lb
(25.9 kg)
	500
	2000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA30XX-1198
	
	
	750
	3000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA25XX-1452
	57 3/16"
(1452 mm)
	67.0 lb
(30.4 kg)
	500
	2500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA37XX-1452
	
	
	750
	3750
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA30XX-1655
	65 3/16"
(1655 mm)
	79.0 lb
(35.8 kg)
	500
	3000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLA45XX-1655
	
	
	750
	4500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	


1 208V = 75% of wattage at 240V.

2 If the control option "24V electronic relay" is required, these products need two electronic relays.

3 If the control option "24V electronic relay" is required, these products need three electronic relays.
4 XX = 08 (208V, 1 ph), 38 (208V, 3 ph), 00 (240V), 30 (240V, 3PH), 77 (277V), 07 (347V), 04 (480V, 1PH), 34 (480V, 3PH), 06 (600V, 1 ph), 36 (600V, 3 ph).
( = Available.

Add "BL" for white, "AM" for almond.
Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD
	Clean back
	

	KIT-OLA-CI
	-
	Corner (Inside and outside)
	

	KIT-OLA-CR-27
	-
	Recess trim kit, 27 3/16 in. (690 mm)
	

	KIT-OLA-CR-37
	-
	Recess trim kit, 37 3/16 in. (944 mm)
	

	KIT-OLA-CR-47
	-
	Recess trim kit, 47 3/16 in. (1198 mm)
	

	KIT-OLA-CR-57
	-
	Recess trim kit, 57 3/16 in. (1452 mm)
	

	KIT-OLA-CR-65
	-
	Recess trim kit, 65 3/16 in. (1655 mm)
	

	KIT-OLA-CTR
	-
	Relay box, 12 in. (305 mm)
	

	-
	FR
	Front warm air outlet
	

	KIT-OLA-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	KIT-OLA-SO-27
	-
	Sub-base, 27 3/16 in. (690 mm)
	

	KIT-OLA-SO-37
	-
	Sub-base, 37 3/16 in. (944 mm)
	

	KIT-OLA-SO-47
	-
	Sub-base, 47 3/16 in. (1198 mm)
	

	KIT-OLA-SO-57
	-
	Sub-base, 57 3/16 in. (1452 mm)
	

	KIT-OLA-SO-65
	-
	Sub-base, 65 3/16 in. (1655 mm)
	

	KIT-OLA-SV-27
	-
	Empty cabinet, 27 3/16 in. (690 mm)
	

	KIT-OLA-SV-37
	-
	Empty cabinet, 37 3/16 in. (944 mm)
	

	KIT-OLA-SV-47
	-
	Empty cabinet, 47 3/16 in. (1198 mm)
	

	KIT-OLA-SV-57
	-
	Empty cabinet, 57 3/16 in. (1452 mm)
	

	KIT-OLA-SV-65
	-
	Empty cabinet, 65 3/16 in. (1655 mm)
	

	Controls
	
	
	

	-
	CTT
	Single-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	CTT2
	Double-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	DIS403
	Disconnect switch, triple-pole, 40A at 600V
	

	-
	PM
	Pneumatic relay, 20A at 600V
	

	KIT-OLA-R
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OLA-R2
	R2
	Double-pole relay, coil 24V, without transformer: 25A at 240V - 10A at 600V
	

	KIT-OLA-R2-30
	R230
	Double-pole relay, coil 24V, without transformer, 30A at 600V max.
	

	KIT-OLA-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 4500W, 22A at 208V
	

	KIT-OLA-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 5200W, 22A at 240V
	

	KIT-OLA-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 5200W, 19A at 277V
	

	KIT-OLA-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 6000W, 18A at 347V
	

	KIT-OLA-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 6000W, 10A at 600V (2-wire only)
	

	KIT-OLA-T-AV2
	TAV2
	Single-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	KIT-OLA-T2-AV
	T2AV
	Double-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	-
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer, 15A at 208V, 240V, 277V, 347V
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	Transformers
	
	
	

	-
	TRF24
	Transformer 24V, 50VA
	

	-
	TRF240
	Transformer 240V, 50VA
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 For 1-phase model only.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Electronic relay (1 or 3-phase) available upon request.

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec)  G0R 2C0  CANADA • Phone: 1 800 463-7043 • (418) 247-3947 • Fax: 1 800 662-7801 • (418) 247-7801 • www.ouellet.com • info@ouellet.com


