[image: image1.jpg]




Approval Drawings

Series

OLI
High Density Architectural Sloped Top Cabinet Convector

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 

· Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 

aluminum, semi-gloss black, sand.

· Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
20-gauge steel cabinet.


-
16-gauge steel front cover.

-
Extruded aluminum bar grilles prevent insertion of foreign objects.


-
Front fresh air inlet; top warm air outlet.


-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset.

Heating element
-
Three stainless steel tubular heating elements with aluminum ﬁns.

-
Floating elements on high-temperature nylon bushings, 


reducing expansion noises.

Watt density
-
Average standard watt density of 1000W/ft.

-
Average low watt density of 500W/ft., 750W/ft.

Control
-
Built-in tamperproof thermostat available.

· Mechanical, electronic or pneumatic relays available.
Note: Single-pole thermostat is for 1 phase model only.

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.
Installation
-
Not for residential use in the United States.


-
Wall or ﬂoor mounted installation.

-
Mounting holes spaced on 2 in. (51 mm) intervals for ease of installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit or sub-base available.

Warranty
-
1-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center.
[image: image3.jpg]KOE @22 mm KOE 102 x 52 mm

64 mm
" KOE 4" x 2"
KOE @7/8 184 mm —< - +— 21/2"
KOE @6.4 mm 714" .
KOE @1/4" 58 mm
"' | * _____________ " j KOE @6.4 mm 21/4"
T Y © T 'S} | | KOE @1/4" *‘ r
| !
317 mm )i 204 mm i 512mm -y | \\ 5. 132mm
121/2" min " 51 mm ! 203/16" ) "
" 8 | 53/16
8172 L o | ‘ i - ¥
Y Fay ~ | \4—
l Q i | ";1 mm* KOE ©28-222 mm >1mm
I 152 rom - KOE @1 1/8"-@7/8" 2
Y e * f Y
102 mm 76 mm i L KOE @28-622 mm
4" 3" KOE @1 1/8"-@7/8"

Right Side View Front View Bottom View




Average Standard Watt Density Models 1000W/ft. 

	Watts
	Watts

240/208V1
	Product #
	Length
	Weight

	
	
	208V
(1 ph)
	Qty
	208V
(3 ph)
	Qty
	240/208V
	Qty
	277V
	Qty
	480V
(1 ph)
	Qty
	480V
(3 ph)
	Qty
	in.
	mm
	lb
	kg

	2000
	2000/1500
	OLI2008
	
	OLI20382
	
	OLI2000
	
	OLI2077
	
	OLI2004
	
	OLI20342
	
	27 3/16
	690
	37.0
	16.8

	3000
	3000/2250
	OLI3008
	
	OLI30382
	
	OLI3000
	
	OLI3077
	
	OLI30042
	
	OLI30343
	
	37 3/16
	944
	47.0
	21.3

	4000
	4000/3000
	OLI40082
	
	OLI40382
	
	OLI40002
	
	OLI4077
	
	OLI40042
	
	OLI40343
	
	47 3/16
	1198
	57.0
	25.9

	5000
	5000/3750
	OLI50083
	
	OLI50382
	
	OLI50002
	
	OLI50772
	
	OLI50043
	
	OLI50343
	
	57 3/16
	1452
	67.0
	30.4

	6000
	6000/4500
	OLI60083
	
	OLI60383
	
	OLI60003
	
	OLI60772
	
	OLI60043
	
	OLI60343
	
	65 3/16
	1655
	79.0
	35.8


Average Low Watt Density

	Product #4
	Length
	Weight
	Average

Density W/ft.
	Watts
	208V
(1 ph)
	Qty
	208V
(3 ph)
	Qty
	240V
	Qty
	277V
	Qty
	480V

(1 ph)
	Qty
	480V

(3 ph)
	Qty

	OLI10XX-690
	27 3/16"
(690 mm)
	37.0 lb

(16.8 kg)
	500
	1000
	(
	
	(
	
	(
	
	(
	
	-----
	-----
	-----
	-----

	OLI15XX-690
	
	
	750
	1500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI15XX-944
	37 3/16"
(944 mm)
	47.0 lb

(21.3 kg)
	500
	1500
	(
	
	(
	
	(
	
	(
	
	-----
	-----
	(
	

	OLI22XX-944
	
	
	750
	2250
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI20XX-1198
	47 3/16"
(1198 mm)
	57.0 lb

(25.9 kg)
	500
	2000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI30XX-1198
	
	
	750
	3000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI25XX-1452
	57 3/16"
(1452 mm)
	67.0 lb

(30.4 kg)
	500
	2500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI37XX-1452
	
	
	750
	3750
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI30XX-1655
	65 3/16"
(1655 mm)
	79.0 lb

(35.8 kg)
	500
	3000
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	

	OLI45XX-1655
	
	
	750
	4500
	(
	
	(
	
	(
	
	(
	
	(
	
	(
	


1 208V = 75 % of wattage at 240V.

2 If the control option "24V electronic relay" is required, these products need two electronic relays.
3 If the control option "24V electronic relay" is required, these products need three electronic relays.
4 XX = 08 (208V, 1 ph), 38 (208V, 3 ph), 00 (240V), 30 (240V, 3PH), 77 (277V), 07 (347V), 04 (480V, 1PH), 34 (480V, 3PH), 06 (600V, 1 ph), 36 (600V, 3 ph).
( = Available.

Add "BL" for white, "AM" for almond. Optional colors shown in the color chart section are available upon request.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.
Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD
	Clean back
	

	KIT-OLI-CE
	-
	Outside corner, 8 in. (203.2 mm)
	

	KIT-OLI-CI
	-
	Inside corner, 8 in. (203.2 mm)
	

	KIT-OLI-CTR
	-
	Relay box, 12 in. (305 mm)
	

	KIT-OLI-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	KIT-OLI-SO-27
	-
	Sub-base, 27 3/16 in. (690 mm)
	

	KIT-OLI-SO-37
	-
	Sub-base, 37 3/16 in. (944 mm)
	

	KIT-OLI-SO-47
	-
	Sub-base, 47 3/16 in. (1198 mm)
	

	KIT-OLI-SO-57
	-
	Sub-base, 57 3/16 in. (1452 mm)
	

	KIT-OLI-SO-65
	-
	Sub-base, 65 3/16 in. (1655 mm)
	

	KIT-OLI-SV-27
	-
	Empty cabinet, 27 3/16 in. (690 mm)
	

	KIT-OLI-SV-37
	-
	Empty cabinet, 37 3/16 in. (944 mm)
	

	KIT-OLI-SV-47
	-
	Empty cabinet, 47 3/16 in. (1198 mm)
	

	KIT-OLI-SV-57
	-
	Empty cabinet, 57 3/16 in. (1452 mm)
	

	KIT-OLI-SV-65
	-
	Empty cabinet, 65 3/16 in. (1655 mm)
	

	Controls
	
	
	

	-
	CTT
	Single-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	CTT2
	Double-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	DIS403
	Disconnect switch, triple-pole, 40A at 600V
	

	-
	PM
	Pneumatic relay, 20A at 600V
	

	KIT-OLI-R
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OLI-R2
	R2
	Double-pole relay, coil 24V, without transformer: 25A at 240V - 10A at 600V
	

	KIT-OLI-R2-30
	R230
	Double-pole relay, coil 24V, without transformer, 30A at 600V max.
	

	KIT-OLI-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 4500W, 22A at 208V
	

	KIT-OLI-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 5200W, 22A at 240V
	

	KIT-OLI-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 5200W, 19A at 277V
	

	KIT-OLI-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 6000W, 18A at 347V
	

	KIT-OLI-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 6000W, 10A at 600V (2-wire only)
	

	KIT-OLI-T-AV2
	TAV2
	Single-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	KIT-OLI-T2-AV
	T2AV
	Double-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	-
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer, 15A at 208V, 240V, 277V, 347V
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	Transformers
	
	
	

	-
	TRF24
	Transformer 24V, 50VA
	

	-
	TRF240
	Transformer 240V, 50VA
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 For 1-phase model only.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Electronic relay (1 or 3-phase) available upon request.

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

