[image: image4.jpg]@DUELLET



[image: image4.jpg]

Approval Drawings

Series

OMB
Mini Aluminum Draft Barrier


[image: image1.jpg]


[image: image2.jpg]




Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, aluminum, 
semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.


-
Optional: anodized aluminum.

Voltage
-
208V, 240/208V, 277V, 347V, 480V, 600V, 50/60 Hz, 1-phase.
Construction
-
14-gauge (0.0787 in. [2 mm]) aluminum front cover.


-
18-gauge satin coat steel cabinet.


-
Screw assembly for added strength.


-
Full length built-in wireway.


-
Separate low voltage wireway (-WW) available.


-
Pencil-proof openings less than 1/4 in. (6.4 mm).


-
Bottom fresh air inlet; top warm air outlet.


-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset. 



High altitude version available (-HA).


-
End caps included.

Heating element
-
Stainless steel tubular heating element with aluminum fins.

-
Floating heating element on high-temperature nylon bushings


reducing expansion noises.

Watt density
-
Average standard watt density of 175W/ft.

-
Average low watt density of 100W/ft., 150W/ft.

Control
-
Built-in thermostat available with a control knob or tamperproof.

· Mechanical, electronic or pneumatic relays available (installed on the right end only).
Ouellet highly recommends to use an electronic wall thermostat for greater comfort.

Installation
-
Not for residential use in the United States.


-
Heater must be installed at least 2 in. (51 mm) from finished floor.


-
Mounting holes spaced on 4 in. (102 mm) intervals for ease of installation.


-
Installation on wall or ﬂoor mounted with pedestals.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit available.

Warranty
-

3-year warranty against defects.

Application
-
Commercial building, office building, hospital, daycare center private residence.
[image: image3.jpg]64 mm
21/2"

0 E=——/

Side View Front View
> 2>
64 mm ° e N —| == °
212" . o o — ) (O
28 mm)| < <
1178 94 mm
33/4"

Bottom View

Standard Finish
Clean Back (-BD) on the Back of the Heater
]
1 s T
a f f o "N 1  120mm
|t 434"
{ | b © e (Q | ‘
KOE @22 mm L J L27 mm
KOE @7/8" 122mm = q4/16"
413/16

Rear View




Average Standard Watt Density Models 175W/ft.
	Watts
	Watts

240/208V1
	Product #
	Length
	Weight

	
	
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	350
	350/263
	OMB0358
	
	OMB0350
	
	-
	-
	-
	-
	27 9/16
	700
	7.0
	3.2

	525
	525/394
	OMB0528
	
	OMB0520
	
	OMB0527
	
	-
	-
	35 7/16
	900
	8.3
	3.8

	700
	700/526
	OMB0708
	
	OMB0700
	
	OMB0707
	
	-
	-
	47 1/4
	1200
	10.2
	4.6

	875
	875/657
	OMB0878
	
	OMB0870
	
	OMB0807
	
	OMB0876
	
	59 1/16
	1500
	12.0
	5.5

	1050
	1050/789
	OMB1058
	
	OMB1050
	
	OMB1057
	
	OMB1056
	
	70 7/8
	1800
	13.9
	6.3

	1225
	1225/920
	OMB1228
	
	OMB1220
	
	OMB1227
	
	OMB1226
	
	82 11/16
	2100
	15.8
	7.2

	1400
	1400/1052
	OMB1408
	
	OMB1400
	
	OMB1407
	
	OMB1406
	
	94 1/2
	2400
	17.6
	8.0


Average Low Watt Density Models
	Product #2
	Length
	Weight
	Average

Density W/ft.
	Watts
	Watts

240/208V1
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty

	OMB030X-700
	27 9/16"

(700 mm)
	7.0 lb
(3.2 kg)
	150
	300
	300/225
	(
	
	(
	
	-----
	-----
	-----
	-----

	OMB030X-900
	35 7/16"
(900 mm)
	8.3 lb
(3.8 kg)
	100
	300
	300/225
	(
	
	(
	
	-----
	-----
	-----
	-----

	OMB045X-900
	
	
	150
	450
	450/338
	(
	
	(
	
	(
	
	-----
	-----

	OMB040X-1200
	47 1/4"
(1200 mm)
	10.2 lb
(4.6 kg)
	100
	400
	400/300
	(
	
	(
	
	(
	
	-----
	-----

	OMB060X-1200
	
	
	150
	600
	600/450
	(
	
	(
	
	(
	
	-----
	-----

	OMB050X-1500
	59 1/16"
(1500 mm)
	12.0 lb
(5.5 kg)
	100
	500
	500/375
	(
	
	(
	
	(
	
	(
	

	OMB075X-1500
	
	
	150
	750
	750/563
	(
	
	(
	
	(
	
	(
	

	OMB060X-1800
	70 7/8"

(1800 mm)
	13.9 lb
(6.3 kg)
	100
	600
	600/450
	(
	
	(
	
	(
	
	(
	

	OMB090X-1800
	
	
	150
	900
	900/675
	(
	
	(
	
	(
	
	(
	

	OMB070X-2100
	82 11/16"
(2100 mm)
	15.8 lb
(7.2 kg)
	100
	700
	700/525
	(
	
	(
	
	(
	
	(
	

	OMB105X-2100
	
	
	150
	1050
	1050/788
	(
	
	(
	
	(
	
	(
	

	OMB080X-2400
	94 1/2"
(2400 mm)
	17.6 lb
(8.0 kg)
	100
	800
	800/600
	(
	
	(
	
	(
	
	(
	

	OMB120X-2400
	
	
	150
	1200
	1200/900
	(
	
	(
	
	(
	
	(
	


1 208V = 75% of wattage at 240V.

2 X = 8 (208V), 0 (240/208V), 77 (277V), 7 (347V), 4 (480V), 6 (600V).
( = Available.
Add "BL" for white, "AM" for almond.
Other colors, accessories and finishes are available upon request. Please contact your customer service representative.
Other voltages available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD3
	Clean back
	

	KIT-OMB-CE
	-
	Outside corner, 4 in. (102 mm)
	

	KIT-OMB-CI
	-
	Inside corner, 4 in. (102 mm)
	

	KIT-OMB-JT
	-
	Splice plate, 2 in. (51 mm)
	

	KIT-OMB-JT-PE
	-
	Contour splice plate for BD option and1or heater with pedestals, 2 in. (51 mm)
	

	KIT-OMB-PE
	-
	Round pedestal kit (2), 3 in. (76 mm)
	

	KIT-OMB-PEC
	-
	Square-shaped pedestal kit (2), 2 in. (51 mm)
	

	OMB-SV-XX
	-
	Empty cabinet with length of XX mm (minimum: 154 mm, maximum: 2400 mm)
	

	Controls
	
	
	

	KIT-OMB-DIS204
	DIS204
	Disconnect switch, 20A at 277V max.
	

	-
	HA
	Linear high-limit temperature control for high altitude (3000 ft. to 8200 ft.)
	

	-
	PM
	Pneumatic relay, 20A at 600V max.
	

	KIT-OMB-R-347
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OMB-R-600
	R
	Single-pole relay, coil 24V, without transformer, 12.5A at 480V, 10A at 600V
	

	KIT-OMB-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V
	

	KIT-OMB-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V
	

	KIT-OMB-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V
	

	KIT-OMB-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V
	

	KIT-OMB-RT-6002
	RT2
	Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only)
	

	KIT-OMB-TB6
	TB6
	Single-pole bi-metal thermostat: 25A at 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-OMB-TB261
	TB261
	Double-pole bi-metal thermostat: 25A at 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-OMB-TB6-AV
	TB6AV
	Single-pole bi-metal tamperproof thermostat: 25A at 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-OMB-TB26-AV1
	TB26AV1
	Double-pole bi-metal tamperproof thermostat: 25A at 208V, 240V, 277V - 10A at 347V, 480V, 600V
	

	KIT-OMB-TRIAC-347
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	KIT-OMB-TRIAC-347T
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 277V, 347V
	

	KIT-OMB-TRIAC-600
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	-
	WW
	24V wireway
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 "Off" position.

2 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

3 For anodized aluminum heaters, the clean back option will be fixed with visible rivets.

4 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 
Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

