[image: image1.jpg]




Approval Drawings

Series

OPA
Architectural Cabinet Convector

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 


aluminum, semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240/208V, 277V, 347V, 480V, 600V, 1-phase.

Construction
-
20-gauge steel cabinet.


-
16-gauge steel front cover.


-
Extruded aluminum bar grilles prevent insertion of foreign objects.


-
Front fresh air inlet; top warm air outlet.



- Front warm air outlet  available (-FR).

-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset.

Heating element
-
Two stainless steel tubular heating elements with aluminum ﬁns.

-
Floating elements on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 500W/ft.

-
Average low watt density of 375W/ft.
Control
-
Built-in tamperproof thermostat available.

· Mechanical, electronic or pneumatic relays available.
Ouellet highly recommends use of an electronic wall  thermostat for greater comfort.

Installation
-
Not for residential use in the United States.


-
Wall or ﬂoor mounted installation.

-
Front outlet -FR models may be recessed.


-
Mounting holes spaced on 2 in. (51 mm) intervals for ease of installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit or sub-base available.

Warranty
-
1-year warranty against defects.
Application
-
Commercial building, office building, hospital, daycare center.

[image: image3.jpg]KOE @6.4 mm
KOE @1/4"

KOE @22 mm

KOE @7/8"

‘f

204 mm1024,r,"m

81/32"

b

i
—o

Right Side View

KOE @6.4 mm

58 mm

21/4"

132mm

KOE @1/4" *‘ r 53/16"

BN

}
T
\
\
T

\‘?

> L KOE @28-@22 mm -J < 51 mm
51 mm KOE @1 1/8"-@7/8" 2"
o
Bottom View

Unit with Front Grilles (-FR)

191 mm

Unit with Grille on Top

Recessed 712" Not Recessed
|
357 mm
14"
114 mm k 76 mm J
“ KOE ©28-@22 mm 3
4172 KOE @1 1/8"-@7/8"
Front View





Average Standard Watt Density Models 500W/ft.

	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	208V
	Qty
	240/208V
	Qty
	277V
	Qty
	480V
	Qty
	in.
	mm
	lb
	kg

	1000
	1000/750
	OPA1008
	
	OPA1000
	
	OPA1077
	
	OPA1004
	
	27 3/16
	690
	30.0
	13.6

	1500
	1500/1125
	OPA1508
	
	OPA1500
	
	OPA1577
	
	OPA1504
	
	37 3/16
	944
	46.0
	20.9

	2000
	2000/1500
	OPA2008
	
	OPA2000
	
	OPA2077
	
	OPA2004
	
	47 3/16
	1198
	57.0
	25.9

	2500
	2500/1875
	OPA2508
	
	OPA2500
	
	OPA2577
	
	OPA2504
	
	57 3/16
	1452
	66.0
	29.9

	3000
	3000/2250
	OPA3008
	
	OPA3000
	
	OPA3077
	
	OPA30041
	
	65 3/16
	1655
	75.0
	34.0

	3500
	3500/2625
	OPA35081
	
	OPA3500
	
	OPA3577
	
	OPA35041
	
	75 3/16
	1909
	80.0
	36.3

	4000
	4000/3000
	OPA40081
	
	OPA40001
	
	OPA4077
	
	OPA40041
	
	83 1/8
	2112
	89.0
	40.4


Average Low Watt Density Models 375W/ft. 

	Watts
	Product #
	Length
	Weight

	
	208V
	Qty
	240V
	Qty
	277V
	Qty
	480V
	Qty
	in.
	mm
	lb
	kg

	800
	OPA0808-690
	
	OPA0800-690
	
	OPA0877-690
	
	OPA0804-690
	
	27 3/16
	690
	30.0
	13.6

	1000
	OPA1008-944
	
	OPA1000-944
	
	OPA1077-944
	
	OPA1004-944
	
	37 3/16
	944
	46.0
	20.9

	1500
	OPA1508-1198
	
	OPA1500-1198
	
	OPA1577-1198
	
	OPA1504-1198
	
	47 3/16
	1198
	57.0
	25.9

	1750
	OPA1758-1452
	
	OPA1750-1452
	
	OPA1777-1452
	
	OPA1754-1452
	
	57 3/16
	1452
	66.0
	29.9

	2000
	OPA2008-1655
	
	OPA2000-1655
	
	OPA2077-1655
	
	OPA2004-1655
	
	65 3/16
	1655
	75.0
	34.0

	2500
	OPA2508-2112
	
	OPA2500-2112
	
	OPA2577-2112
	
	OPA2504-2112
	
	83 1/8
	2112
	89.0
	40.4

	2750
	OPA2758-2112
	
	OPA2750-2112
	
	OPA2777-2112
	
	OPA2754-21121
	
	83 1/8
	2112
	89.0
	40.4


1If the control option "24V electronic relay" is required, these products need two electronic relays.

2 208V = 75% of wattage at 240V.

Add "BL" for white, "AM" for almond. Optional colors shown in the color chart section are available upon request.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.

Other low watt density models available upon request.
Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD
	Clean back
	

	KIT-OPA-CI
	-
	Corner (inside and outside)
	

	KIT-OPA-CR-27
	-
	Recess trim kit, 27 3/16 in. (690 mm)
	

	KIT-OPA-CR-37
	-
	Recess trim kit, 37 3/16 in. (944 mm)
	

	KIT-OPA-CR-47
	-
	Recess trim kit, 47 3/16 in. (1198 mm)
	

	KIT-OPA-CR-57
	-
	Recess trim kit, 57 3/16 in. (1452 mm)
	

	KIT-OPA-CR-65
	-
	Recess trim kit, 65 3/16 in. (1655 mm)
	

	KIT-OPA-CR-75
	-
	Recess trim kit, 75 3/16 in. (1909 mm)
	

	KIT-OPA-CR-83
	-
	Recess trim kit, 83 1/8 in. (2112 mm)
	

	KIT-OPA-CTR
	-
	Relay box, 12 in. (305 mm)
	

	-
	FR
	Front warm air outlet
	

	KIT-OPA-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	KIT-OPA-SO-27
	-
	Sub-base, 27 3/16 in. (690 mm)
	

	KIT-OPA-SO-37
	-
	Sub-base, 37 3/16 in. (944 mm)
	

	KIT-OPA-SO-47
	-
	Sub-base, 47 3/16 in. (1198 mm)
	

	KIT-OPA-SO-57
	-
	Sub-base, 57 3/16 in. (1452 mm)
	

	KIT-OPA-SO-65
	-
	Sub-base, 65 3/16 in. (1655 mm)
	

	KIT-OPA-SO-75
	-
	Sub-base, 75 3/16 in. (1909 mm)
	

	KIT-OPA-SO-83
	-
	Sub-base, 83 1/8 in. (2112 mm)
	

	KIT-OPA-SV-27
	-
	Empty cabinet, 27 3/16 in. (690 mm)
	

	KIT-OPA-SV-37
	-
	Empty cabinet, 37 3/16 in. (944 mm)
	

	KIT-OPA-SV-47
	-
	Empty cabinet, 47 3/16 in. (1198 mm)
	

	KIT-OPA-SV-57
	-
	Empty cabinet, 57 3/16 in. (1452 mm)
	

	KIT-OPA-SV-65
	-
	Empty cabinet, 65 3/16 in. (1655 mm)
	

	KIT-OPA-SV-75
	-
	Empty cabinet, 75 3/16 in. (1909 mm)
	

	KIT-OPA-SV-83
	-
	Empty cabinet, 83 1/8 in. (2112 mm)
	

	Controls
	
	
	

	-
	CTT
	Single-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	CTT2
	Double-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	DIS402
	Disconnect switch, triple-pole, 40A at 600V
	

	-
	PM
	Pneumatic relay, 20A at 600V
	

	KIT-OPA-R
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OPA-R2
	R2
	Double-pole relay, coil 24V, without transformer: 25A at 240V - 10A at 600V
	

	KIT-OPA-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 4500W, 22A at 208V
	

	KIT-OPA-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 5200W, 22A at 240V
	

	KIT-OPA-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 5200W, 19A at 277V
	

	KIT-OPA-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 6000W, 18A at 347V
	

	KIT-OPA-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 6000W, 10A at 600V (2-wire only)
	

	KIT-OPA-T-AV
	TAV
	Single-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	KIT-OPA-T2-AV
	T2AV
	Double-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	-
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer, 15A at 208V, 240V, 277V, 347V
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	Transformers
	
	
	

	-
	TRF24
	Transformer 24V, 50VA
	

	-
	TRF240
	Transformer 240V, 50VA
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

