[image: image1.jpg]




Approval Drawings

Series

OPI
Architectural Sloped Top Cabinet Convector

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Color
-
Standard: white, almond. 


-
Optional (upcharge applicable): metallic silver, bronze, metallic charcoal, 


aluminum, semi-gloss black, sand.


-
Custom colors available upon request.

Finish
-
Standard: epoxy/polyester powder paint.

Voltage
-
208V, 240/208V, 277V, 347V, 480V, 600V, 1-phase.

Construction
-
20-gauge steel cabinet.


-
16-gauge steel front cover.


-
Extruded aluminum bar grilles prevent insertion of foreign objects.


-
Front fresh air inlet; top warm air outlet.


-
Clean back available (-BD).


-
Linear high-limit temperature control with automatic reset.

Heating element
-
Two stainless steel tubular heating elements with aluminum ﬁns.

-
Floating elements on high-temperature nylon bushings 


reducing expansion noises.

Watt density
-
Average standard watt density of 500W/ft.

-
Average low watt density of 375W/ft.
Control
-
Built-in tamperproof thermostat available.

· Mechanical, electronic or pneumatic relays available.
Ouellet highly recommends use of an electronic wall  thermostat for greater comfort.

Installation
-
Not for residential use in the United States.


-
Wall or ﬂoor mounted installation.

-
Mounting holes spaced on 2 in. (51 mm) intervals for ease of installation.


-
Variety of accessories available for wall-to-wall installation.


-
Pedestal kit or sub-base available.

Warranty
-
3-year warranty against defects.
Application
-
Commercial building, office building, hospital, daycare center.

[image: image3.jpg]KOE @6.4 mm
KOE @1/4"

KOE @22 mm
KOE @7/8"

204 mm
81/32"

73mm -
27/8"

Right Side View

102 mm
4

216 mm
81/2"

19T mm
712"

6o o o

51 mm

o 2"

3

57 mm
14"

114 mm
41/2"

T
X KOE @28-@22 mm
KOE @1 1/8"-@7/8"

Front View

76 mm
3n

58 mm
KOE @6.4 mm 21/4"
KOE @1/4"
| 1r
| \
| i
-k KOE @28-222 mm -
51mm KOE @1 1/8"-@7/8" 51 mm
2 o
Bottom View

132 mm
53/16"




Average Standard Watt Density Models 500W/ft. 

	Watts
	Watts

240/208V2
	Product #
	Length
	Weight

	
	
	208V
	Qty
	240/208V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	1000
	1000/750
	OPI1008
	
	OPI1000
	
	OPI1007
	
	OPI1006
	
	27 3/16
	690
	32.0
	14.5

	1500
	1500/1125
	OPI1508
	
	OPI1500
	
	OPI1507
	
	OPI1506
	
	37 3/16
	944
	46.0
	20.9

	2000
	2000/1500
	OPI2008
	
	OPI2000
	
	OPI2007
	
	OPI2006
	
	47 3/16
	1198
	57.0
	25.9

	2500
	2500/1875
	OPI2508
	
	OPI2500
	
	OPI2507
	
	OPI2506
	
	57 3/16
	1452
	66.0
	30.0

	3000
	3000/2250
	OPI3008
	
	OPI3000
	
	OPI3007
	
	OPI3006
	
	65 3/16
	1655
	75.0
	34.1

	3500
	3500/2625
	OPI35081
	
	OPI3500
	
	OPI3507
	
	OPI3506
	
	75 3/16
	1909
	80.0
	36.3

	4000
	4000/3000
	OPI40081
	
	OPI40001
	
	OPI4007
	
	OPI40061
	
	83 1/8
	2112
	89.0
	40.5


Average Low Watt Density Models 375W/ft. 

	Watts
	Product #
	Length
	Weight

	
	208V
	Qty
	240V
	Qty
	347V
	Qty
	600V
	Qty
	in.
	mm
	lb
	kg

	800
	OPI0808-690
	
	OPI0800-690
	
	OPI0807-690
	
	OPI0806-690
	
	27 3/16
	690
	32.0
	14.5

	1000
	OPI1008-944
	
	OPI1000-944
	
	OPI1007-944
	
	OPI1006-944
	
	37 3/16
	944
	46.0
	20.9

	1500
	OPI1508-1198
	
	OPI1500-1198
	
	OPI1507-1198
	
	OPI1506-1198
	
	47 3/16
	1198
	57.0
	25.9

	1750
	OPI1758-1452
	
	OPI1750-1452
	
	OPI1757-1452
	
	OPI1756-1452
	
	57 3/16
	1452
	66.0
	30.0

	2000
	OPI2008-1655
	
	OPI2000-1655
	
	OPI2007-1655
	
	OPI2006-1655
	
	65 3/16
	1655
	75.0
	34.1

	2500
	OPI2508-2112
	
	OPI2500-2112
	
	OPI2507-2112
	
	OPI2506-2112
	
	83 1/8
	2112
	89.0
	40.5

	2750
	OPI2758-2112
	
	OPI2750-2112
	
	OPI2757-2112
	
	OPI2756-2112
	
	83 1/8
	2112
	89.0
	40.5


1If the control option "24V electronic relay" is required, these products need two electronic relays.

2 208V = 75% of wattage at 240V.

Add "BL" for white, "AM" for almond.
Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.

Other low watt density models available upon request.

Options
	Product # 

Kit
	Product # 

Factory installed*
	Description
	Qty

	Finish
	
	
	

	-
	BD
	Clean back
	

	KIT-OPI-CE
	-
	Outside corner, 8 in. (203.2 mm)
	

	KIT-OPI-CI
	-
	Inside corner, 8 in. (203.2 mm)
	

	KIT-OPI-CTR
	-
	Relay box, 12 in. (305 mm)
	

	KIT-OPI-PEC
	-
	Square-shaped pedestal kit (2), 3 in. (76 mm)
	

	KIT-OPI-SO-27
	-
	Sub-base, 27 3/16 in. (690 mm)
	

	KIT-OPI-SO-37
	-
	Sub-base, 37 3/16 in. (944 mm)
	

	KIT-OPI-SO-47
	-
	Sub-base, 47 3/16 in. (1198 mm)
	

	KIT-OPI-SO-57
	-
	Sub-base, 57 3/16 in. (1452 mm)
	

	KIT-OPI-SO-65
	-
	Sub-base, 65 3/16 in. (1655 mm)
	

	KIT-OPI-SO-75
	-
	Sub-base, 75 3/16 in. (1909 mm)
	

	KIT-OPI-SO-83
	-
	Sub-base, 83 1/8 in. (2112 mm)
	

	KIT-OPI-SV-27
	-
	Empty cabinet, 27 3/16 in. (690 mm)
	

	KIT-OPI-SV-37
	-
	Empty cabinet, 37 3/16 in. (944 mm)
	

	KIT-OPI-SV-47
	-
	Empty cabinet, 47 3/16 in. (1198 mm)
	

	KIT-OPI-SV-57
	-
	Empty cabinet, 57 3/16 in. (1452 mm)
	

	KIT-OPI-SV-65
	-
	Empty cabinet, 65 3/16 in. (1655 mm)
	

	KIT-OPI-SV-75
	-
	Empty cabinet, 75 3/16 in. (1909 mm)
	

	KIT-OPI-SV-83
	-
	Empty cabinet, 83 1/8 in. (2112 mm)
	

	Controls
	
	
	

	-
	CTT
	Single-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	CTT2
	Double-pole relay, coil 240V: 25A at 240V, 10A at 600V
	

	-
	DIS402
	Disconnect switch, triple-pole, 40A at 600V
	

	-
	PM
	Pneumatic relay, 20A at 600V
	

	KIT-OPI-R
	R
	Single-pole relay, coil 24V, without transformer: 22A at 208V, 240V - 19A at 277V - 18A at 347V
	

	KIT-OPI-R2
	R2
	Double-pole relay, coil 24V, without transformer: 25A at 240V - 10A at 600V
	

	KIT-OPI-RT-208
	RT
	Single-pole relay, coil 24V, with transformer 208V/24V, 4500W, 22A at 208V
	

	KIT-OPI-RT-240
	RT
	Single-pole relay, coil 24V, with transformer 240V/24V, 5200W, 22A at 240V
	

	KIT-OPI-RT-277
	RT
	Single-pole relay, coil 24V, with transformer 277V/24V, 5200W, 19A at 277V
	

	KIT-OPI-RT-347
	RT
	Single-pole relay, coil 24V, with transformer 347V/24V, 6000W, 18A at 347V
	

	KIT-OPI-RT-6001
	RT1
	Single-pole relay, coil 24V, with transformer 600V/24V, 6000W, 10A at 600V (2-wire only)
	

	KIT-OPI-T-AV
	TAV
	Single-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	KIT-OPI-T2-AV
	T2AV
	Double-pole tamperproof thermostat: 30A at 250V max. - 15A at 600V max.
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 15A at 347V max.
	

	-
	TRIACT
	Single-pole electronic relay, coil 24V, with transformer, 15A at 208V, 240V, 277V, 347V
	

	-
	TRIAC
	Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max.
	

	Transformers
	
	
	

	-
	TRF24
	Transformer 24V, 50VA
	

	-
	TRF240
	Transformer 240V, 50VA
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

