[image: image1.png]


[image: image3.png]Thermoscreens





Approval Drawings

Series

ORA-C
C Range Commercial Air Curtain

[image: image4.jpg]@DUELLET





Features

Model
-
Electric heat.

-
No heat.
Color
-
Standard: white.
· Custom colors available upon request (RAL Chart).
Voltage
-
208V, 240/208V, 480V, 600V, 60 Hz.
Construction
-
Steel casing with resistant plastic end caps.

-
Quick access to the internal components thanks to the front panel which facilitate maintenance and connection.

-
High-limit temperature control with automatic reset.
Fan
-
Tangential fans.
Heating element
-
Element provides instant heat (electric model).
Control
-
Touch remote control included (20 ft. (6 m) RJ control cable included).
· Door switch included.
· Compatible with a Building Management System (Bacnet MS/TP, Modbus RTU or dry contact).
· Personalize programing of the air curtain.
Installation
- 
Minimum height installation: 6 ft. (1.8 m).


-
Maximum height installation: 


- Surface-mounted: 9.84 ft. (3 m) above the floor.



- Recessed: 9 ft. (2.75 m) above the floor.

-
Surface-mounted: brackets included.

-
Ceiling hanging: fixings are included for 1/4 in. x 20 UNC threaded rods (rods not supplied).


-
Recessed: hinged core grilles included for easy installation and maintenance.

-
Joining kit, available in option, for connecting multiple surface mounted units.
Warranty
-
2-year warranty against defects. 

Application
-
Vestibule, commercial building, entrance way, service door, hospital.
[image: image2.png]E
G % F F
.l_ 39 ) ju‘ 20 mm‘
. . 08" |
8 mm |
= = 03" §
Back View
: — Entry points for
- electrical supply
D < < . D and controls
70 mm
120 rr:m =0 2.8"
4.7 | o - . ; T33 m"m
Inserts for 1/4 UNC drop rods, g 13
4for 1m unit, 6 for 1.5m/2m units T};L/VZV/ 12 |n.tl§SPP Remote control
connections
. el dmp%h—ol-eso . connection interface
727, 72, 77,
Z%Bm..m Top View
C1000 C1500 C2000
mm | in. [ mm in. [ mm in.
A 11371 44.8 | 1669 | 65.7 |2200 | 86.6
B 908 | 35.8 11408 | 554 1928 | 759
C - - 704 27.7 | 964 38.0
D 115 | 45 | 131 5.2 136 54
E 710 | 28.0 (1208 | 47.6 | 1748 | 68.8
F 0 0 604 23.8 | 874 344
G 214 | 84 | 231 9.1 226 8.9
H 152 6 172 6.8 172 6.8

275 mm
10.8"

Side View

Recessed

| 10 mm 10mm
1.9 04— —Ioa
@) |
i
[l ¥ . B
: Az Ceiling e e R W
| NN\ c l
353 mm
139" Back View
Entry points for electrical
25mmto75mm supply and controls
1"to 3
Side View B D
22 mm A /
0.9" |
5\ \g i 313 mm
13"
257 mmi| |44 Holes for M3 / 5/16 in. threaded :8
10.1" suspension rods at each corner f
Rp1/2/1/2in. BSPP / 165 mm
LPHW connections .} 6.5
Top View
C1000 C1500 C2000
mm| po |mm| po |mm]| po
A 1129| 444 |1529]| 60.2 |2040| 80.3
B 1179| 464 |1579]| 62.2 |2090| 82.3
C 1209| 47.6 |1609| 63.3 |[2120| 83.5
Cut-Out | Length [1179| 464 |1579| 62.2 [2090| 82.3
in Ceiling | Width |301 |11.85[301 | 11.85 | 301 | 11.85





IMPORTANT: 600V and 480V models need 2 power sources (E.g.: 600V+208V or 230V) or an external transformer (E.g.: 600V/240V).
The VA requirement varies between models: C1000 = 200VA, C1500 and C2000 = 350VA.

Models
	Product #
	Qty
	Volts (ph)
	kW

Lo/Hi
	Amp.
	cfm
	Max velocity (ft./min)
	dBA at 3 m
	Effective width 

of air stream
	Weight

	
	
	
	
	
	
	
	
	in.
	mm
	lb
	kg

	Surface-mounted

	Electric heat

	C1000ESEC600V
	
	600 (3) + 2402
	4.5/9
	9.3+0.5
	740
	1770
	55.0
	36
	933
	35
	16

	C1500ESEC600V
	
	600 (3) + 2402
	6/12
	12.8+0.7
	1060
	1770
	55.0
	56
	1430
	51
	23

	C2000ESEC600V
	
	600 (3) + 2402
	9/18
	18.6+1.0
	1470
	1770
	56.0
	78
	1996
	73
	33

	C1000ESEC480V
	
	480 (3) + 2402
	4.5/9
	10.9+0.5
	740
	1770
	55.0
	36
	933
	35
	16

	C1500ESEC480V
	
	480 (3) + 2402
	6/12
	14.5+0.7
	1060
	1770
	55.0
	56
	1430
	51
	23

	C2000ESEC480V
	
	480 (3) + 2402
	9/18
	21.7+1.0
	1470
	1770
	56.0
	78
	1996
	73
	33

	C1000ESEC208V
	
	208 (3)3
	4.32/8.64
	24.5
	740
	1770
	55.0
	36
	933
	35
	16

	C1500ESEC208V
	
	208 (3)3
	5.77/11.53
	32.7
	1060
	1770
	55.0
	56
	1430
	51
	23

	C2000ESEC208V
	
	208 (3)3
	8.64/17.28
	49.0
	1470
	1770
	56.0
	78
	1996
	73
	33

	No heat

	C1000ASEC208-230V
	
	208/240 (1)3
	-
	0.5
	740
	1770
	55.0
	36
	933
	33
	15

	C1500ASEC208-230V
	
	208/240 (1)3
	-
	0.7
	1060
	1770
	55.0
	56
	1430
	46
	21

	C2000ASEC208-230V
	
	208/240 (1)3
	-
	1
	1470
	1770
	56.0
	78
	1996
	68
	31

	Recessed

	Electric heat

	C1000EREC600V
	
	600 (3) + 2402
	4.5/9
	9.3+0.5
	740
	1770
	55.0
	45
	1145
	44
	20

	C1500EREC600V
	
	600 (3) + 2402
	6/12
	12.8+0.7
	1060
	1770
	55.0
	60
	1545
	60
	27

	C2000EREC600V
	
	600 (3) + 2402
	9/18
	18.6+1.0
	1470
	1770
	56.0
	80
	2055
	82
	37

	C1000EREC480V
	
	480 (3) + 2402
	4.5/9
	10.9+0.5
	740
	1770
	55.0
	45
	1145
	44
	20

	C1500EREC480V
	
	480 (3) + 2402
	6/12
	14.5+0.7
	1060
	1770
	55.0
	60
	1545
	51
	23

	C2000EREC480V
	
	480 (3) + 2402
	9/18
	21.7+1.0
	1470
	1770
	56.0
	80
	2055
	73
	33

	C1000EREC208V
	
	208 (3)3
	4.32/8.64
	24.5
	740
	1770
	55.0
	45
	1145
	44
	20

	C1500EREC208V
	
	208 (3)3
	5.77/11.53
	32.7
	1060
	1770
	55.0
	60
	1545
	60
	27

	C2000EREC208V
	
	208 (3) 3
	8.64/17.28
	 49.0 
	1470
	1770
	56.0
	80
	2055
	82
	37

	No heat

	C1000AREC208V
	
	208/240 (1)3
	-
	0.5
	740
	1770
	55.0
	45
	1145
	42
	19

	C1500AREC208V
	
	208/240 (1)3
	-
	0.7
	1060
	1770
	55.0
	60
	1545
	55
	25

	C2000AREC208V
	
	208/240 (1)3
	-
	1
	1470
	1770
	56.0
	80
	2055
	77
	35


1 To order any custom colors from the R.A.L. chart, add “-SP” at the end of the Product # and specify RAL color # on the order. Contact our customer service department 
for lead times.

2 IMPORTANT: 600V and 480V models need 2 power sources (E.g.: 600V + 230V) or an external transformer (E.g.: 600V/240V). The VA requirement varies between models: 
C1000 = 200VA, C1500 and C2000 = 350VA.
3 Maximum installation height when connected to 208V is 8.53 ft. (2.6 m).

Options
	Product #
	Description
	Qty

	ORA-RS-485
	Cable RS-485 to USB adaptor
	

	ORA-T7263703
	Printed circuit board (PCB) V10
	

	T5951001
	Master and slave lead: 9.84 ft. (3 m)
	

	T5951050
	Ecopower extension lead: 32.80 ft. (10 m)
	

	T5951060
	Ecopower extension lead: 49.21 ft. (15 m)
	

	T5951020
	Ecopower extension lead: 98.42 ft. (30 m)
	

	T5951030
	Extension lead coupler
	


Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	ELectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

