[image: image1.jpg]DN20 (3/4%),
All models outside thread
F/D/B

X

E/C/A

ol

DN20 (3/4) //

2m/6.6 ftunits
Unit without heating or with water heating

b 2%
;I (e e T T T eI T
o| (LECEEEr e e e e e e CTCETACr) - Cenrree e e e e e e CIn
|/ (e e e CCECTCCCCLCACCTETALY)  CCEeerer e e T rLe eI reee
DN20 (3/4)

Unit with electrical heating
L G G K

|
b
jgi%u=u=‘@.f

Metric  Imperial  Type Metric  Imperial
[mm] (in] [mm] (in]
A 2068 8140 PAEC3220Cx J 209 822
B 2045 8050 PAEC3220Cx K 167 657
C 1578 62.10 PAEC3215Cx L 165 649
D 1555 61.20 PAEC3215Cx M 119 468
E 1068 42.00 PAEC3210Cx N 99 3.89
F 1045 4110 PAEC3210Cx o 50 196
G 500 19.68 3 52 200
H 458 18.00 Q 2 165
| 256 10.00 R 10 0.39




[image: image2.png]


[image: image3.png]




Approval Drawings

Series
ORA-EC32
Air curtain for commercial premises


Features
Model
-
Electric heat.

-
No heat.
Color
-
Stainless steel housing: white (RAL 9016, NCS S 0500-N).

-
Grille, rear face and ends grey (RAL 7046).

-
Custom colors available upon request (RAL Chart).
Voltage
-
208V, 480V, 600V, 60 Hz.
Motor
-
Very low operating costs can be achieved thanks to the combination of EC motors and Frico's unique fan geometry.
Construction
-
Quick access to internal components via the maintenance hatch.
· High-limit temperature control with automatic reset.
· Integrated transformer for motor and control circuit (480V and 600V models).
Fan
-
Squirrel-cage fans.
Element
-
Element provides instant heat (electric heat model).
Control
-
Integrated control system and additional easy to use remote control.
· Door switch included.
Installation
-
Maximum height installation: 7.2 ft. (2.2 m) above the floor.

- Suspended mounting:

- With pendulum brackets included: 

  
 4 brackets for 1m and 1.5m models and 6 brackets for 2m models.


- With threaded rods (not included).
Note: The recommended installation height may vary according to the installation conditions. Air curtains must be placed as near to the entrance as possible and cover the entire width.

Warranty
-
5-year warranty against defects.
Certification
-
CAN/CSA-E60335-2-30:13 (R2018).
· UL 2021 Ed. 4.0.
· Protection class for units with electrical heating: IP20.
· Protection class for units without heating: IP21.
Application 
- 
Small entrances, vestibule, commercial building, lobby, service door, hospital, store entrance, drive-through, service counters.
[image: image4.jpg]@DUELLET




Models
	Product #
	Qty
	Volts (ph)
	Heat Output

kW

Lo/Hi
	Input Power Motor
	Amp.
	cfm
	dBA2
	Effective air width
	Weight

	
	
	
	
	HP
	
	
	
	in.
	mm
	lb
	kg

	Surface-mounted

	Electric Heat

	PAEC3210CE08-600VNA
	
	600 (3)
	4/8
	9
	1150
	2346
	73
	38.4
	975
	57
	26

	PAEC3215CE12-600VNA
	
	600 (3)
	6/12
	13
	1600
	2267
	72
	58.5
	1486
	82
	37

	PAEC3220CE16-600VNA
	
	600 (3)
	8/16
	17
	2250
	2346
	75
	77.8
	1976
	112
	51

	PAEC3210CE08-480VNA
	
	480 (3)
	4/8
	11
	1150
	2346
	73
	38.4
	975
	57
	26

	PAEC3215CE12-480VNA
	
	480 (3)
	6/12
	16
	1600
	2267
	72
	58.5
	1486
	82
	37

	PAEC3220CE16-480VNA
	
	480 (3)
	8/16
	21
	2250
	2346
	75
	77.8
	1976
	112
	51

	PAEC3210CE07-208VNA
	
	208 (3)
	4/7
	21
	1150
	2346
	73
	38.4
	975
	57
	26

	PAEC3215CE10-208VNA
	
	208 (3)
	7/10
	29
	1600
	2267
	72
	58.5
	1486
	82
	37

	PAEC3220CE13-208VNA
	
	208 (3)
	8/13
	39
	2250
	2346
	75
	77.8
	1976
	112
	51

	No Heat 

	PAEC3210A-NA
	
	208 (1)
	-
	-
	0.6
	765
	70
	30.5
	777.24
	35.3
	16.0

	PAEC3215A-NA
	
	208 (1)
	-
	-
	0.9
	1265
	72
	50.7
	1287.78
	52.9
	24.0

	PAEC3220A-NA
	
	208 (1)
	-
	-
	1.0
	1471
	73
	67.4
	1711.96
	70.5
	32.0

	Surface-mounted

	Electric Heat

	AREC3210CE08-600VNA
	
	600 (3)
	4/8
	9
	950
	2159
	72
	38.2
	970
	68
	31

	AREC3215CE12-600VNA
	
	600 (3)
	6/12
	13
	1350
	2018
	73
	58.5
	1486
	91
	41

	AREC3220CE16-600VNA
	
	600 (3)
	8/16
	17
	1900
	2159
	74
	78.7
	2000
	130
	59

	AREC3210CE08-480VNA
	
	480 (3)
	4/8
	11
	950
	2159
	72
	38.2
	970
	68
	31

	AREC3215CE12-480VNA
	
	480 (3)
	6/12
	16
	1350
	2018
	72
	58.5
	1486
	91
	41

	AREC3220CE16-480VNA
	
	480 (3)
	8/16
	21
	1900
	2159
	74
	78.7
	2000
	130
	59

	AREC3210CE07-208VNA
	
	208 (3)
	4/7
	21
	950
	2159
	72
	38.2
	970
	68
	31

	AREC3215CE10-208VNA
	
	208 (3)
	7/10
	29
	1350
	2018
	73
	58.5
	1486
	91
	41

	AREC3220CE13-208VNA
	
	208 (3)
	8/13
	39
	1900
	2159
	74
	78.7
	2000
	130
	59

	No Heat

	AREC3210A-NA
	
	208 (1)
	-
	-
	0.7
	950
	2159
	72
	38.2
	970
	64

	AREC3215A-NA
	
	208 (1)
	-
	-
	0.9
	1350
	2018
	73
	58.5
	1486
	88

	AREC3220A-NA
	
	208 (1)
	-
	-
	1.4
	1900
	2159
	74
	78.7
	2000
	121


To order any custom colors from the R.A.L. chart, add “SP”’ at the end of the Product # and specify RAL color # on the order. Contact our customer service department for lead times.

Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice
	Project:
	Approval

Information

	Consultant Engineer:
	

	ELectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3rd Avenue, L’Islet (Quebec)  G0R 2C0  CANADA • Phone: 1-800-463-7043 • (418) 247-3947 • Fax: 1-800-662-7801 • (418) 247-7801 • www.ouellet.com • info@ouellet.com

