[image: image1.png]Airflow (cfm)

120
100

N A O ®
S S5 & o

o
S)

0 25

50

Static pressure (Pa)
75 100 125 150 175

20060

Exhaust,

T T
219cfm=1L/s

Supply,

Tin.w.g=250Pa

—{ 50

40

30

20

10

0.1

0.2

03 04 05 06 07
Static pressure (in.w.g.)

0,80

Airflow (L/s)



[image: image4.png]


[image: image5.png]@

21001
HVI CSA-C439-18

CERTIFIED






Approval Drawings

Series
OSALE115

ERV - Energy Recovery Ventilator
Side Port Model                                                                   Top Port Model
[image: image6.png]@oueiier ’

Ve Ery




[image: image7.jpg]Stale air
Out

Fresh air

Fre?rl"\ air 562
221/8
» 594 mm
233/8"

Stale air

Fresh air

Stale air
In

562 mm|
221/8"

594 mm
233/8"








Features
Air flow and performance
-
Fully adjustable air ﬂow (113 cfm @ 0 in.w.g.).

· 64% sensible recovery effectiveness at 0 °C (32 °F) 30 L/s.
Voltage
-
120V, 60Hz, 0.8A.
Benefit
-
Reduce heating demand in winter and cooling demand in summer.


-  Whisper-quiet: factory calibrated and balanced.

-
Easy installation and maintenance.

-
Designed and manufactured in Canada to operate in variable climatic conditions.
Construction
-
Door and housing in corrosion-resistant galvanized steel, 



24-gauge, pre-painted neutral white.

- 
Convenient, screwless hinged door.


-
Ultra-thin: 9 in. (229 mm). 

-  No drain required.

- 
Lightweight for ease of installation: 32 lb (14.5 kg).

- 
Port size: 5 in. (127 mm).

-
Merv8 charcoal polyester filters. Merv13 filters in option (SA-FI-M13).




- 
Two configurations to optimize your space: 
Side Port or Top Port models.
- 
Reverse air flow conﬁguration available as a factory installed option (-R). 

For further explanation, please refer to the document Normal and Reverse.

-
Foam for ceiling installation for Top Port models only, available as a factory 

installed option (-F).

- 
Backdraft damper required on fresh air inlet (not supplied).
Motor
-
Energy-efficient, sealed European motor with closed housing and automatic reset 


thermal protection.
· Balancing without flow keys. 100% electronic adjustment. Pressure ports integrated 


into the door for precise, easy balancing.
Energy recovery core
-
High-efficiency 100% polymer core, extremely durable.


-  Recovers both latent and sensible energy. (Heat and Humidity).

-  Meets or exceeds ASHRAE 90.1-2010. 


-  Washable in soapy water to recover its full effectiveness without deterioration 




or contamination.


-
Antimicrobial protection - ISO846.


 - Avoid virus transfer - ASTM F-1671 tested.


-
Zero crossflow contamination - Certiﬁed according to AHRI 1060.

-
UL94 HB Flammability tested.


Control/timer
-
2 control choices available:


-  Optional Decora-style wall-mounted control/timer (SA-LT15).



    INTERMITENT (20-40) – CONTINUOUS – OFF – Timer (20-40-60 minutes).



-  Optional digital Decora-style wall-mounted control/timer (SA-LCD15).



    
INTERMITENT (20-40) – CONTINUOUS – Humidity – Recirculation – OFF.


Installation
-

Can be ceiling-mounted or suspended.
· Easily installed in the ceiling void or just below the fire-rated ceiling.

· Set of nylon suspension straps included for installation.
-  Steel mounting plate for Top Port with foam models only, 


available as an option (SA-P5).
-
Furnace interconnect plug connector factory installed.
Setting
-
Balance the unit using the supplied instruction named: Balancing.

· All the installer needs are the required flow rates, a manometer, and 5 minutes

to adjust and balance the system.

· Simply specify the air flow rates for LOW SPEED and HIGH SPEED.
- 
The static pressure of the system should ideally be less than or equal to the static 

pressure indicated by the graph for HIGH SPEED.

- 
You don't have to worry about static pressure to limit air flow or adding flow keys as 

other devices. All you must do is provide ducting that doesn't limit maximum flow, 

and the unit's adjustments will allow you to fine-tune flow rates.

Warranty
-
Motor 5-year. Other parts except filters and pre-filters 1-year.
Application 
-
The ideal solution for high-rise apartments and small to medium-size homes, 



when regulations do not require unit certification at -25°C (-13 °F).
· Purifies the air by expelling many pollutants, dust, and allergens to the outside, 


while ensuring an equivalent supply of fresh air in the home.

Important note: No controls are included with the purchase of an ERV or HRV. 


SA-LT15 and SA-LCD15 controls must be purchased separately.
Side Port Model

Top Port Model
ERV OSALE115 - Curves at highest speed
[image: image8.jpg]@DUELLET




Energy ratings - HVI certified
[image: image2.png]Supply
temperature
oc °F

Heating
0 32
0 32
0 32
Cooling
35 95

Air flow
cfm  Lis
53 25
64 30
85 40
51 24

Power

33
38
50

34

Sensible Adjusted
recovery Sensible
(SRE)! Recovery

% %

60 64

64 68

62 66

Total Adjusted total

recovery recovery
efficiency efficiency

52 55

Latent recovery /
moisture transfer

%
52

49
44

55




Models

	Product # 
	cfm
	Recirculation
	SRE1 0 °C (32 °F) 30 L/s
	SRE1 -25 °C (-13 °F) 24 L/s
	Port
	Volts
	Hertz
	Amp.
	Weight

	
	
	
	
	
	in.
	mm
	
	
	
	lb
	kg

	ERV energy recovery ventilator 113 cfm Side Port

	OSALE115S
	113
	No
	64%
	No
	5
	127
	120
	60
	0.8
	32
	14.5

	ERV energy recovery ventilator 113 cfm Top Port

	OSALE115T
	113
	No
	64%
	No
	5
	127
	120
	60
	0.8
	32
	14.5


1 SRE: Sensitive Recovery Effectiveness.
Options
	Product # 

Kit
	Product #  

Factory installed*
	Description
	Qty

	-
	-F
	Foam only for ERV Top Port
	

	-
	-R
	Reverse air flow
	

	KIT-SA-FI-115
	-
	Kit of 2 Merv8 filters for ERV 115R
	

	SA-FI-M13
	-
	Merv13 filter for ERV 115-115R-150
	

	SA-P5
	-
	Steel mounting plate only for ERV 115-150 Top Port with foam
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

Controls (sold separately)
	Product # 
	Description
	Qty

	SA-LCD152
	Digital Decora-style wall-mounted control/timer for residential ERV and HRV
	

	SA-LT152
	Decora-style wall-mounted control/timer for residential ERV and HRV
	


2 Must be purchased separately.
Others

	Type
	Quantity
	Model and description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrical Contractor:
	

	Distributor:
	

	Date:
	

	Contact at manufacturer:
	

	Comments:


[image: image3.jpg]



180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

