[image: image1.jpg]Stale air
Out

Fresh air

562 mm
221/8"

648 mm

251/2"

149 mm
4X @57/8"



[image: image5.png]@

21001
HVI CSA-C439-18

CERTIFIED



[image: image6.png]-25°C
-13°F






Approval Drawings

[image: image7.png]VRE[ERY




Series
OSAME230R

ERV - Energy Recovery Ventilator with Recirculation
Side Port Model



Features
Air flow and performance
-
Fully adjustable air ﬂow (230 cfm @ 0 in.w.g.).

· 68% sensible recovery effectiveness at 0 °C (32 °F) 30 L/s, 


58% sensible recovery effectiveness at -25 °C (-13 °F) 26 L/s
· Recirculation defrosts.
Voltage
-
120V, 60Hz, 1.1A.
Benefit
-
Reduce heating demand in winter and cooling demand in summer.


-  Whisper-quiet: factory calibrated and balanced.

-
Easy installation and maintenance.

-
Designed and manufactured in Canada to operate in variable climatic conditions.
Construction
-
Door and housing in corrosion-resistant galvanized steel, 



24-gauge, pre-painted neutral white.

- 
Convenient, screwless hinged door.


-
Ultra-thin: 12 in. (305 mm). 

-  No drain required.

- 
Lightweight for ease of installation: 43 lb (19.5 kg).

- 
Port size: 6 in. (152 mm).

- 
Merv8 charcoal polyester filters.




- 
Side Port model only.
- 
Reverse air flow conﬁguration available as a factory installed option (-R). 

For further explanation, please refer to the document Normal and Reverse.
- 
Backdraft damper required on fresh air inlet (not supplied).
Motor
-
Energy-efficient, sealed European motor with closed housing and automatic reset 


thermal protection.
· Balancing without flow keys. 100% electronic adjustment. Pressure ports integrated 


into the door for precise, easy balancing.
Energy recovery core
-
High-efficiency 100% polymer core, extremely durable.


-  Recovers both latent and sensible energy. (Heat and Humidity).

-  Meets or exceeds - ASHRAE 90.1-2010. 


-  Washable in soapy water to recover its full effectiveness without deterioration or 



contamination.


-
Antimicrobial protection - ISO846.


 - Avoid virus transfer - ASTM F-1671 tested.


-
Zero crossflow contamination - Certiﬁed according to AHRI 1060


-
UL94 HB Flammability tested.


Control/timer
-
2 control choices available:



-  Optional Decora-style wall-mounted control/timer (SA-LT15).



    INTERMITENT (20-40) – CONTINUOUS – OFF – Timer (20-40-60 minutes).



-  Optional digital Decora-style wall-mounted control/timer (SA-LCD15).



    
INTERMITENT (20-40) – CONTINUOUS – Humidity – Recirculation – OFF.


Installation
-

Can be ceiling-mounted or suspended.

· Easily installed in the ceiling void or just below the fire-rated ceiling.

· Set of nylon suspension straps included for installation.
· Furnace interconnect plug connector factory installed.
Setting
-
Balance the unit using the supplied instruction named: Balancing.

· All the installer needs are the required flow rates, a manometer, and 5 minutes to

adjust and balance the system.

· Simply specify the air flow rates for LOW SPEED and HIGH SPEED.
- The static pressure of the system should ideally be less than or equal to the static 

pressure indicated by the graph for HIGH SPEED.

- You don't have to worry about static pressure to limit air flow or adding flow keys as 

other devices. All you must do is provide ducting that doesn't limit maximum flow, 

and the unit's adjustments will allow you to fine-tune flow rates.

Warranty
-
Motor 5-year. Other parts except filters and pre-filters 1-year.
Application 
-
The ideal solution for high-rise apartments and medium-size homes.
· Purifies the air by expelling many pollutants, dust, and allergens to the outside, 


while ensuring an equivalent supply of fresh air in the home.

Important note: No controls are included with the purchase of an ERV or HRV. 


SA-LT15 and SA-LCD15 controls must be purchased separately.
Side Port Model 
[image: image8.jpg]@DUELLET




ERV OSAME230R - Curves at highest speed
[image: image2.png]Airflow (cfm)

2

2

@
S

=)
=3

50

00

v
S

=3

Static pressure (Pa)

1180

94.4

708

flow (L/s)

47.2

ir

Ai

236

0

0 25 50 75 100 125 150 175 200 225 250 275
T T T
Exhiaust 219cfm=1L/s
Tinw.g=250Pa —
Supply
0 01 02 03 04 05 06 07 08 09 10 1.1

Static pressure (in.w.g.)




Energy ratings - HVI certified

[image: image3.png]Supply
temperature
S °F

Heating
0 32
0 32
0 32
-25 -13

Cooling

35 95

Air flow
fm  Lis
47 22
64 30
85 40
55 26
47 22

Power

62
76
90
81

62

Sensible Adjusted
recovery Sensible
(SRE) Recovery
% %
70 79
68 76
66 73
58 62
Total Adjusted total
recovery recovery
efficiency efficiency
56 62

Latent recovery /
moisture transfer

%

67
61
56
56

63




Model

	Product # 
	cfm
	Recirculation
	SRE1 0 °C (32 °F) 
30 L/s
	SRE1 -25 °C (-13 °F) 
26 L/s
	Port
	Volts
	Hertz
	Amp.
	Weight

lb
kg

	
	
	
	
	
	in.
	mm
	
	
	
	

	ERV energy recovery ventilator 230 cfm with recirculation Side Port

	OSAME230RS
	230
	Yes
	68%
	58%
	6
	152
	120
	60
	1.1
	43
	19.5


1 SRE: Sensitive Recovery Effectiveness.
Options
	Product # 

Kit
	Product #  

Factory installed*
	Description
	Qty

	-
	-R
	Reverse air flow
	

	KIT-OSA-INS-6
	-
	Basic installation kit for ERV and HRV, 6 in. (152 mm) ducts
	

	KIT-SA-FI-230
	-
	Kit of 2 Merv8 filters for ERV 230R
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

Controls (sold separately)
	Product # 
	Description
	Qty

	SA-LCD152
	Digital Decora-style wall-mounted control/timer for residential ERV and HRV
	

	SA-LT152
	Decora-style wall-mounted control/timer for residential ERV and HRV
	


2 Must be purchased separately.
Others

	Type
	Quantity
	Model and description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrical Contractor:
	

	Distributor:
	

	Date:
	

	Contact at manufacturer:
	

	Comments:


[image: image4.jpg]



180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

