Series

OSKHE130R

ERV - Energy Recovery Ventilator with Recirculation

Top Port Model

Features

Air flow and performance	-	Air ﬂow 130 cfm at 0.2 in.w.g.

- 75% sensible recovery effectiveness at 0 °C (32 °F) 30 L/s,

60% sensible recovery effectiveness at -25 °C (-13 °F) 27 L/s.

- Recirculation defrosts.

Voltage	-	120V, 60Hz, 1.5A, 172W.

Benefit	-	Reduce heating demand in winter and cooling demand in summer.

-  Whisper-quiet: factory calibrated and balanced.

-	Easy installation and maintenance.

-	Designed and manufactured in Canada to operate in variable climatic conditions.

Construction	-	Door and housing in corrosion-resistant galvanized steel,

24-gauge, pre-painted neutral white.

- 	Convenient, screwless hinged door.

-	Ultra-thin: 14 1/8 in. (359 mm).

- 	Easy installation: 64 lb (29.1 kg).

-  No drain required.

- 	Port size: 5 in. (127 mm).

- 	Top port model only.

- 	Merv8 washable filters. Merv13 washable filter in option (SK-FI-M13).

Motor	-	Energy-efficient, sealed European motor with closed housing and automatic reset

thermal protection.

- Balancing without flow keys. 100% electronic adjustment. Pressure ports integrated

into the door for precise, easy balancing.

Energy recovery core	-	Polymer counterflow energy recovery core offers high energy efficiency for superior performance.

-  Washable in soapy water to recover its full effectiveness without deterioration

or contamination.

Control/timer	-	2 control choices available:

-  Optional Decora-style wall-mounted control/timer (SA-LT15).

INTERMITENT (20-40) – CONTINUOUS – OFF – Timer (20-40-60 minutes).

-  Optional digital Decora-style wall-mounted control/timer (SA-LCD15).

INTERMITENT (20-40) – CONTINUOUS – Humidity – Recirculation – OFF.

Installation	-		Can be wall-mounted or suspended.

- Set of nylon suspension straps included for installation.

- Fits into a 24 in. (610 mm) deep wardrobe.

- Removable terminal block for connection to a furnace, supplied with the device.

Setting	-	Balance the unit using the supplied instruction.

- All the installer needs are the required flow rates, a manometer,

and 5 minutes to adjust and balance the system.

- Simply specify the air flow rates for LOW SPEED and HIGH SPEED.

- The static pressure of the system should ideally be less than or equal to the static

pressure indicated by the graph for HIGH SPEED.

- You don't have to worry about static pressure to limit air flow or adding flow keys as

other devices. All you must do is provide ducting that doesn't limit maximum flow,

and the unit's adjustments will allow you to fine-tune flow rates.

Warranty	-	Motor 5-year. Other parts except filters and pre-filters 1-year.

Application 	-	The ideal solution for high-rise apartments and small to medium-size homes.

-  The most efficient energy recovery ventilator on the market. Ideal for projects

requiring very high energy performance to benefit from all available credits and

subsidies.

- Purifies the air by expelling many pollutants, dust, and allergens to the outside,

while ensuring an equivalent supply of fresh air in the home.

Important note: No controls are included with the purchase of an ERV or HRV. SA-LT15 and SA-LCD15 controls must be purchased separately.

OSKHE130R

Top Port Model

Fresh air

Stale air

ERV OSKHE130R - Curves at highest speed

Ventilation performance at highest speed

| in. wg (Pa) | 0.2 (50) | 0.3 (75) | 0.4 (100) | 0.5 (125) |
| --- | --- | --- | --- | --- |
|  | cfm (L/s) | cfm (L/s) | cfm (L/s) | cfm (L/s) |
| Net supply air flow | 129 (61) | 121 (57) | 113 (53) | 104 (49) |
| Gross supply air flow | 133 (62) | 124 (58) | 116 (54) | 107 (50) |
| Gross exhaust air flow | 151 (71) | 140 (66) | 129 (61) | 118 (56) |

Energy ratings - HVI certified

| Supply temperature |  | Air flow |  | Power | Sensible recovery (SRE)1 | Adjusted sensible recovery | Latent recovery / moisture transfer |
| --- | --- | --- | --- | --- | --- | --- | --- |
| °C | °F | cfm | L/s | W | % | % | % |
| Heating |  |  |  |  |  |  |  |
| 0 | 32 | 49 | 23 | 66 | 78 | 87 | 86 |
| 0 | 32 | 64 | 30 | 76 | 75 | 84 | 81 |
| 0 | 32 | 84 | 40 | 92 | 73 | 80 | 77 |
| -25 | -13 | 58 | 27 | 82 | 60 | 64 | 72 |
| Cooling |  |  |  |  | Total recovery efficiency | Adjusted total recovery efficiency |  |
| 35 | 95 | 64 | 30 | 76 | 68 | 74 | 77 |

Model

| Product # | cfm | Recirculation | SRE1 0 °C (32 °F) 30 L/s | SRE1 -25 °C (-13 °F) 27 L/s | Port |  | Volts | Hertz | Amp. | Weight |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | in. | mm |  |  |  | lb | kg |
| ERV energy recovery ventilator 130 cfm with recirculation Top Port |  |  |  |  |  |  |  |  |  |  |  |
| OSKHE130RT | 130 | Yes | 75% | 60% | 5 | 127 | 120 | 60 | 1.5 | 64 | 29.1 |

1 SRE: Sensitive Recovery Effectiveness.

Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| KIT-OSA-INS-5 | - | Basic installation kit for ERV and HRV, 5 in. (127 mm) ducts |  |
| KIT-SA-FI-150 | - | Kit of 2 Merv8 washable filters for ERV 130R and HRV 150R |  |
| KIT-SK-DRAIN | - | Drain connection kit for ERV and HRV |  |
| SK-FI-M13 | - | Merv13 washable filter for ERV 130R and HRV 150R |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

Controls sold separately

| Product # | Description | Qty |
| --- | --- | --- |
| SA-LT152 | Decora-style wall-mounted control/timer for residential ERV and HRV |  |
| SA-LCD152 | Digital Decora-style wall-mounted control/timer for residential ERV and HRV |  |

2 Must be purchased separately

### Others

| Type | Quantity | Model and description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |  |