[image: image1.jpg]@DUELLET



[image: image2.png]ELSR-MA-XX-1-XX output ELSR-MA-XX-2-XX output

(on insulated metallic pipes, in accordance with IEEE 515/CSA 22.2 130-03) (on insulated metallic pipes, in accordance with IEEE 515/CSA 22.2 130-03)
107
8 .|
€ €
= =S
g g
p=3 p=3
o) o)
T T T T I T T T T T 1 r T T T 1
-40 -30 -20 -10 0 10 20 30 40 50 60 -40 -30 -20 -10 0 10 20 30 40 50 60
(-40) (-22) (4 (14 (32) (500 (68) (86) (104) (122) (140) (-40) (-22) (-4) (14 (32) (50) (68) (86) (104) (122) (140

Pipe temperature °C (°F) Pipe temperature °C (°F)



[image: image1.jpg]

Approval Drawings

Series
OSR-MA
 Micro Self-Regulating Heating Cable ELSR-MA
[image: image3.png]ELSR-MA-3-XX-BF

(in a filled water pipeline)

7 -

Output (W/ft)

T T T T T T T T T T
0 2 4 6 8 10 12 14 14 18 20
(32) (356) (39.2) (428) (464) (50) (53,6) (57,2) (60,8) (644) (68)

Pipe temperature °C (°F)



[image: image4.emf]








[image: image5.png]eltherm’ =

innovations in heat tracing



[image: image6.png]







AO

[image: image7.png]- eoredEs




[image: image8.emf]











BO
[image: image9.png]




BF

Features 
Outer jacket
-
Thermoplastic (AO, BO), Fluoropolymer (BF).
Bus wire
-
Nickel plated copper, 18 AWG.
Minimum start-up

temperature
- -30 °C (-22 °F).
Maximum operating
temperature (power on)
- 60 °C (140 °F).
Maximum continuous 
exposure temperature 
(power off)
- 60 °C (140 °F).
Nominal voltage
- 120V, 240/208V.
Bending radius, min.
- 25 mm (1 in.).
Installation temperature, min.     -
AO, BO: -45 °C (-49 °F).

-
BF: -25 °C (-13 °F).
Standard
-
IEEE 515, CSA 22.2 130.03.
Certification
- 
FM CUS 3050047.
Rating
-  Wet rated, for outdoor use (WS) (AO, BO).
· PS (2000 kPa/290 psi) (BF).

Warranty
-
1-year basic warranty on the heating cable. 

Application
-
Heat tracing of metallic and non-metallic pipes, pumps, vessels and valves, 
food processing industry, automotive, refrigeration, sprinkler systems, sewage pipes, intake drain pipes, potable water line (BF).
Heating Circuit Length for ELSR-MA Models
	120V
	
	240V

	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for
	
	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for

	
	
	ELSR-MA-3-1-XX
	ELSR-MA-5-1-XX
	
	
	
	ELSR-MA-3-2-XX
	ELSR-MA-5-2-XX

	10 °C

(50 °F)
	10
	208
	132
	
	10 °C

(50 °F)
	10
	415
	320

	
	15
	233
	190
	
	
	15
	415
	346

	
	20
	233
	190
	
	
	20
	415
	346

	
	25
	233
	190
	
	
	25
	415
	346

	0 °C

(32 °F)
	10
	170
	110
	
	0 °C

(32 °F)
	10
	379
	273

	
	15
	213
	174
	
	
	15
	379
	320

	
	20
	213
	174
	
	
	20
	379
	320

	
	25
	213
	174
	
	
	25
	379
	320

	-10 °C

(14 °F)
	10
	146
	94
	
	-10 °C

(14 °F)
	10
	325
	239

	
	15
	197
	150
	
	
	15
	349
	299

	
	20
	197
	161
	
	
	20
	349
	299

	
	25
	197
	161
	
	
	25
	349
	299

	-30 °C

(-22 °F)
	10
	113
	73
	
	-30 °C

(-22 °F)
	10
	255
	190

	
	15
	172
	117
	
	
	15
	307
	266

	
	20
	172
	141
	
	
	20
	307
	266

	
	25
	172
	141
	
	
	25
	307
	266



Heating Circuit Length for ELSR-MA-BF Models
	120V
	
	240V
	
	

	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for
	
	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for
	
	

	
	
	ELSR-MA-3-1-BF
	
	
	
	ELSR-MA-3-2-BF
	
	

	10 °C

(50 °F)
	10
	139
	
	10 °C

(50 °F)
	10
	241
	
	

	
	15
	167
	
	
	15
	302
	
	

	
	20
	167
	
	
	20
	302
	
	

	
	25
	167
	
	
	25
	302
	
	

	0 °C

(32 °F)
	10
	112
	
	0 °C

(32 °F)
	10
	202
	
	

	
	15
	153
	
	
	15
	282
	
	

	
	20
	153
	
	
	20
	282
	
	

	
	25
	153
	
	
	25
	282
	
	


Maximum heating circuit ELSR-MA-XX on the following conditions:
• 120/240 Voltage
• MCB type QO (100% utilization)
• Voltage drop max. 10%
• Single cable fed 1 end

Eltherm® Correction Factors/Multipliers for Operation of Heating Cables in 208V

To calculate the corrected power output for operation in 208V, multiply the published output at 240V (in W/ft.) by the nominal output factor provided for the applicable heating cable type.

To calculate maximum heating circuit lengths for operation in 208V (tables provided in product data sheets), multiply the published max. heating circuit length at 240V provided for the applicable heating cable type.

	Heating Cable

Correction Factors/ Multipliers
	Nominal Output

208V vs. 240V
	Heating Circuit Length

208V vs. 240V

	ELSR-MA-XX-2
	0.82
	1.00


OSR Series ELSR-MA Models
	Nominal

Output

W/ft.
	Product #
	Outer jacket/Mechanical shield 
	Cable dimension approx. (mm)

	
	120V1, 3
	240V1, 2, 3
	AO
	Qty
	BO
	Qty
	BF
	Qty
	

	3
	ELSR-MA-3-1-XX
	ELSR-MA-3-2-XX
	(
	
	(
	
	(
	
	7.7 x 6.4

	5
	ELSR-MA-5-1-XX
	ELSR-MA-5-2-XX
	(
	
	(
	
	-
	-
	8.1 x 5.8


1  XX = Outer jacket/Mechanical shield.
  AO Aluminum foil and a thermoplastic outer jacket.
  BO Protective braid and a thermoplastic outer jacket.
  BF Protective braid, suitable for use in potable water (certified according to NSF/ANSI 61).
2 For operations at 208V, please consult Correction Factors/Multipliers. 
3 When ordering, the quantity on the purchase order is equal to the length in feet of the cable required.

  E.g.: To order a 500 ft., cable, write 500 for quantity with product code.

Custom cutting service available for all lengths other than 500 ft. and 1000 ft. (minimum of 25 ft.).

Options
	Product #
Kit
	Description
	Qty

	OSR-MA Models 

(AO and BO outer jacket)
	
	

	EL-ECM1
	End termination for ELSR-MA 
	

	ELVB-SRAM
	Power connection without cable gland
	

	ELVB-SRAM-34-ST
	Power connection with steel/zinc cable gland/fitting, 3/4'' NPT, non-hazardous location
	

	KIT-OSR-ELSR-MA
	End and power termination kit with warning sticker MA Series
	

	OSR-MA Models 

(BF outer jacket)
	
	

	EL-ECMF2
	End termination for ELSR-MA-BF
	

	KIT-OSR-ECA-MABF-PH-FIT
	Brass gland cable fitting 3/4’’ NPT non-hazardous location for MA-BF cable
	

	KIT-OSR-ELSR-MA-BF
	End and power termination kit with warning sticker BF Series
	

	KIT-OSR-MABF-PH-1-CTSOD3
	Quick connect plumbing kit for 1” OD polyethylene CTS pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-114-CTSOD3
	Quick connect plumbing kit for 1 1/4” OD polyethylene CTS pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-112-CTSOD3
	Quick connect plumbing kit for 1 1/2” OD polyethylene CTS pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-34-ID3
	Quick connect plumbing kit for 3/4” ID polyethylene pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-1-ID3
	Quick connect plumbing kit for 1” ID polyethylene pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-114-ID3
	Quick connect plumbing kit for 1 1/4” ID polyethylene pipes for MA-BF cable
	

	KIT-OSR-MABF-PH-112-ID3
	Quick connect plumbing kit for 1 1/2” ID polyethylene pipes for MA-BF cable
	

	Multiple applications
	
	

	KIT-OSR-EL-WS03
	Warning label/sign bilingual (English / French)
	

	Roof and gutter
	
	

	ELB-20
	Downspout 90° mounting plate
	

	ELB-21
	Gutter mounting plate
	

	ELB-RCLIP-B
	Roof clips black anodized, package of 25
	

	Pipe tracing
	
	

	ELB-02B
	Self-adhesive glass fiber tape, max. temp. = 90 °C (194 °F), 50 m (165 ft.)
	

	ELB-06C
	Self-adhesive aluminum tape, max. temp. = 80 °C (176 °F), 50 m (165 ft.)
	


1 Minimum installation temperature -45 °C (-49 °F).
2 Minimum installation temperature -13 °C (-25 °F).
3 Identifying the type of pipe is key to ensuring a simple and effective connection, Ouellet Canada is not responsable for incorrect pipe selection. No returns will be accepted.
Controls

	Product #
	Description
	Qty

	Controller options for roof and gutter for de-icing 

	DS-2C1
	Aerial mounted controller with sensor to detect humidity and temperature, 30A, 100V to 277V
	

	DS-8C1
	Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 
30A, 100V to 277V
	

	DS-9C1
	Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 
2 X 30A, 100V to 277V
	

	EX-50
	50 ft. (15 m) extension kit, with connection fittings for humidity sensor
	

	CDP-2
	Interior controller and display for DS products
	

	ETO21
	Dual-zone electronic controller, 3 X 16A, 120V to 240V
	

	ETF-744/99
	24V outdoor sensor for measuring temperature
	

	ETOR-55
	Gutter sensor to detect humidity with 33 ft. (10 m) cable
	

	Controller options for pipe tracing for use in non-hazardous (ordinary) locations

	ECA-E55-R25HT1
	SPDT, NEMA 4X thermostat in molded aluminum housing, 22A at 120/250/480V, with 10 ft. (3 m) stainless steel bulb and capillary
	

	TPR-L1N-3X-Q101
	SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 3 ft. (1 m) tinned copper bulb 
and capillary
	

	TPR-L1N-10X-Q101
	SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 10 ft. (3 m) tinned copper bulb 
and capillary
	

	TRF115-0051
	SPDT, NEMA 4X thermostat, range -17 °C to 49 °C (0 °F to 120 °F), 25A at 120/208/240/277V, with 5 ft. (1.5 m) stainless bulb 
and capillary
	

	TRF115-0071
	SPDT, NEMA 4X thermostat, range -35 °C to 38 °C (-30 °F to 100 °F), 25A at 120/208/240/277V, with 8 ft. (2.4 m) copper bulb 
and capillary
	

	ELTC-14-RTD1
	Digital temperature control 20A at 90-260V, including 3-wire RTD (Pt-100) sensing element is 5x50mm with 5m of fluoropolymer lead wires, range 0 to 250°C
	

	GPT-130
	Single point heat trace control thermostat NEMA 4X c/w GFEP and a 20 ft. thermistor 30A@100-277V
	

	S1-A
	NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP 

and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet, Modbus and BACnet3 capabilities
	

	S1-B
	NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP 

and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet
	

	GATEWAY-PCKG
	24VDC BACnet gateway assembly with power supply NEMA 4X enclosure with 24VDC transformer for S1 Series
	

	GATEWAY
	24VDC BACnet gateway stand alone for S1 Series
	

	Controller options for pipe tracing for use in non-hazardous (ordinary) and hazardous locations

	TXR-L2S-10-Q101
	SPDT, explosion-proof, NEMA 4, 7 and 9 thermostat, in anodized aluminum housing, 22A at 120/250/480V, 

with 10 ft. (3 m) stainless steel bulb and capillary
	

	TM-1SIH1-E5-RTD-A1
	TraceMateTM I GFCI electronic thermostat for single circuit at 120V
	

	TM-1DIH2-E5-RTD-A1
	TraceMateTM I GFCI electronic thermostat for single circuit at 240/208V
	

	TM-2SIH1-E5-RTD
	TraceMateTM II GFCI electronic thermostat for dual circuit at 120V
	

	TM-2DIH2-E5-RTD
	TraceMateTM II GFCI electronic thermostat for dual circuit at 240/208V
	

	MS-21012
	MasterTrace Single circuit electronic GFCI controller with double pole, 85V to 280V, 30A, with user interface
	

	MS-21022
	MasterTrace Double circuit electronic GFCI controller with single pole, 120V or 277V, 30A, with user interface
	

	RTD-7
	RTD probe for MasterTrace controller
	

	Control panel options

	SR-4CIR-240
	4 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.)
	

	SR-6CIR-240
	6 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.)
	

	SR-8CIR-240
	8 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x20x8 in.)
	

	SR-12CIR-240
	12 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x24x8 in.)
	


1 Requires a ground fault circuit interrupter (GFCI) in the electrical panel.
2 Requires a RTD probe for MasterTrace controller (RTD-7).
3 BACnet IP or MS/TP available via preconfigured SMC gateway, sold separately.
Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electricial Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


ELSR-MA-BF








180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

