[image: image1.jpg]@DUELLET



[image: image2.png]eltherm’ =

innovations in heat tracing



[image: image1.jpg]

Approval Drawings

Series
OSR-PI
120V Preassembled Self-Regulating Heating Cable
[image: image3.png]


[image: image4.png]



[image: image5.png]Linear power output in air cond
to operating temperature

Power cutput (WAL

% 0 o 1 on B o 0 ©
@ @ 0y @ 60 6 @ a4 (2 040





Features 
Nominal voltage
-
120V.

Cold lead length
-
36’’ (0.9 m).
Outer jacket
-
Thermoplastic.
Bus wire
-
Nickel plated copper.
Maximum operating

temperature (power on)
-
60 °C (140 °F).
Maximum continuous 
exposure temperature 
(power off)
-
80 °C (176 °F).
Cable section
-
14.1 mm X 5.6 mm.
Bending radius, minimum
-
25 mm (1 in.).
Included hardware
- Grounded 3-pronged plug with indicator light to show when the cable is on.

Installation
-  Never cut or shorten the heating cable.

· Installation accessories sold separately.

Minimum installation and

start-up temperature
-
-25 °C (-13 °F).
Standards
- 
CSA C22.2.130.03; -WS.

· CAN/CSA 60079-7:12, 60079-0-11.

· ANSI/IEEE 515, 515.
Certification
- 
CSA C US 2547790
Rating
-  Wet rated, for outdoor use (WS).


Warranty
-
1-year basic warranty on the heating cable. 

Application
-
Freeze protection, roof and gutter, pipes.


Options

	Product #

Kit
	Description
	Qty

	Roof and gutter
	
	

	ELB-20
	Downspout 90° mounting plate
	

	ELB-21
	Gutter mounting plate
	

	ELB-RCLIP-B
	Roof clips black anodized, package of 25
	

	Pipe tracing
	
	

	ELB-02B
	Self-adhesive glass fiber tape, max. temp. = 90 °C (194 °F), 50 m (165 ft.)
	

	ELB-06C
	Self-adhesive aluminum tape, max. temp. = 80 °C (176 °F), 50 m (165 ft.)
	


Models
	Product #1
	Length
	Nominal power output 
in air condition at 5 °C (40 °F)2
	Qty

	
	ft.
	m
	Watts
	

	ECK-7AO-006
	6
	1.8
	42
	

	ECK-7AO-012
	12
	3.6
	84
	

	ECK-7AO-018
	18
	5.5
	126
	

	ECK-7AO-025
	25
	7.6
	175
	

	ECK-7AO-050
	50
	15.2
	350
	

	ECK-7AO-075
	75
	22.9
	525
	

	ECK-7AO-100
	100
	30.5
	700
	


1 Must be plugged into a 120V outlet fitted with ground fault protection device (GFCI). 
2 Because of the cable's self-regulating properties, the power density can reach up to 11 Watts per foot when buried in snow or ice: "wet density". In this situation, use of a 15 Amp. circuit breaker is valid for all models.
Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electricial Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

