[image: image2.emf]







[image: image3.png]eltherm’ =

innovations in heat tracing



[image: image4.png]




Approval Drawings

Series
OSR-WA
Medium Temperature Self-Regulating 

Heating Cable ELSR-WA
[image: image5.jpg]@DUELLET




 

    AO



    BO

Features 
Outer jacket
-
Thermoplastic (AO, BO).
Bus wire
-
Nickel plated copper.
Minimum start-up

temperature
- -30 °C (-22 °F).
Maximum operating
temperature (power on)
- 80 °C (176 °F).
Maximum continuous 
exposure temperature 
(power off)
- 90 °C (194 °F).
Nominal voltage
-
120V, 240/208V.
Bending radius, min.
-
20 mm (3/4 in.).
Installation temperature, min.     - -45 °C (-49 °F).
Classification
-
Class I, Zone 1, AEx / Ex e II, T5.


-
Class I, Division 2, Groups A, B, C, D.

-
Class II, Division 1, Groups E, F, G.

-
Class III, Division 1.
Standards
- 
IEEE CUS 3050047.
Certification
- 
FM CUS 3050047.
Rating
-  Wet rated, for outdoor use (WS).

Warranty
-
1-year basic warranty on the heating cable. 

Application
-
Freeze protection of heated lines or pipes, food processing industry, 
drain lines in canteens and large scale kitchens, hot water supply installations.
Heating Circuit Length for ELSR-WA Models
	120V
	
	240V

	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for
	
	Start-up temperature
	CB capacity (A)
	Maximum heating circuit length (ft.) for

	
	
	ELSR-WA-55-1
	ELSR-WA-65-1
	
	
	
	ELSR-WA-55-2
	ELSR-WA-65-2

	10 °C

(50 °F)
	10
	144
	97
	
	10 °C

(50 °F)
	10
	231
	149

	
	15
	219
	145
	
	
	15
	348
	226

	
	20
	246
	194
	
	
	20
	430
	302

	
	25
	246
	198
	
	
	25
	430
	348

	
	30
	246
	198
	
	
	30
	430
	348

	0 °C

(32 °F)
	10
	131
	87
	
	0 °C

(32 °F)
	10
	207
	136

	
	15
	197
	133
	
	
	15
	312
	203

	
	20
	233
	176
	
	
	20
	405
	272

	
	25
	233
	189
	
	
	25
	405
	326

	
	30
	233
	189
	
	
	30
	405
	326

	-10 °C

(14 °F)
	10
	118
	81
	
	-10 °C

(14 °F)
	10
	187
	123

	
	15
	180
	121
	
	
	15
	279
	184

	
	20
	221
	160
	
	
	20
	372
	247

	
	25
	221
	180
	
	
	25
	384
	310

	
	30
	221
	180
	
	
	30
	384
	312

	-30 °C

(-22 °F)
	10
	102
	68
	
	-30 °C

(-22 °F)
	10
	158
	105

	
	15
	153
	103
	
	
	15
	237
	160

	
	20
	202
	139
	
	
	20
	315
	212

	
	25
	203
	167
	
	
	25
	353
	263

	
	30
	203
	167
	
	
	30
	353
	286


Maximum heating circuit ELSR-WA-XX on the following conditions:
• 120/240 Voltage
• MCB type QO (100% utilization)
• Voltage drop max. 10%
• Single cable fed 1 end
[image: image1.png]ELSR-WA-XX-1-XX output
(on insulated metallic pipes, in accordance with IEEE 515/CSA 22.2 130-03)

12

107

\i
4
2

Output (W/ft)

T T T T T T T T T T T 1
-40 -30 -20 -10 0 10 20 30 40 50 60 70 80

(-40) (-22) (4 (14 (32) (50) (68) (86) (104) (122) (140) (158) (176)

Pipe temperature °C (°F)

ELSR-WA-XX-2-XX output
(on insulated metallic pipes, in accordance with IEEE 515/CSA 22.2 130-03)

Output (W/ft)

r T T T T

40 -30 -20 -10 O 10 20 30 40 50 60 70 80

(-40) (-122) (9 (149 (32) (50) (68) (86) (104) (122) (140) (158) (176)
Pipe temperature °C (°F)




Eltherm® Correction Factors/Multipliers for Operation of Heating Cables in 208V

To calculate the corrected power output for operation in 208V, multiply the published output at 240V (in W/ft.) by the nominal output factor provided for the applicable heating cable type.

To calculate maximum heating circuit lengths for operation in 208V (tables provided in product data sheets), multiply the published max. heating circuit length at 240V provided for the applicable heating cable type.

	Heating Cable

Correction Factors/ Multipliers
	Nominal Output

208V vs. 240V
	Heating Circuit Length

208V vs. 240V

	ELSR-WA-XX-2
	0.80
	1.00



OSR Series ELSR-WA Models
	Application
	Nominal

Output

W/ft.
	Product#
	Outer jacket/Mechanical shield
	Cable dimension approx. (mm)

	
	
	120V1, 3
	240V1, 2, 3
	AO
	Qty
	BO
	Qty
	

	When used for water supply lines
	3
	ELSR-WA-55-1-XX
	ELSR-WA-55-2-XX
	(
	
	(
	
	13.8 x 5.6

	When used for water supply lines
	5
	ELSR-WA-65-1-XX
	ELSR-WA-65-2-XX
	(
	
	(
	
	13.8 x 5.6

	When used with fat/oil lines
	7
	ELSR-WA-65-1-XX
	ELSR-WA-65-2-XX
	(
	
	(
	
	13.8 x 5.6



1  XX = Outer jacket/Mechanical shield.
  AO Aluminum foil and a thermoplastic outer jacket.
  BO Protective braid and a thermoplastic outer jacket.
2 For operations at 208V, please consult Correction Factors/Multipliers. 
3 When ordering, the quantity on the purchase order is equal to the length in feet of the cable required.

  E.g.: To order a 500 ft., cable, write 500 for quantity with product code.

Custom cutting service available for all lengths other than 500 ft. and 1000 ft. (minimum of 25 ft.).


Options
	Product #
Kit
	Description
	Qty

	EL-CLIC-P
	Quick connector with supply lead, for 1 to 3 cables
	

	EL-CLIC-S
	Quick connector for direct connection or cold lead connection of 1 to 3 cables
	

	EL-ECN-EX1
	End termination for ELSR-WA 
	

	ELVB-SRAW
	Power connection without cable gland
	

	ELVB-SRAW-34-ST
	Power connection with steel/zinc cable gland, 3/4'' NPT, non-hazardous location
	

	KIT-OSR-ELSR-WA
	End and power termination kit with warning sticker WA Series
	

	Multiple applications
	
	

	KIT-OSR-EL-WS03
	Warning label/sign bilingual (English / French)
	

	Roof and gutter
	
	

	ELB-20
	Downspout 90° mounting plate
	

	ELB-21
	Gutter mounting plate
	

	ELB-RCLIP-B
	Roof clips black anodized, package of 25
	

	Pipe tracing
	
	

	ELB-02B
	Self-adhesive glass fiber tape, max. temp. = 90 °C (194 °F), 50 m (165 ft.)
	

	ELB-06C
	Self-adhesive aluminum tape, max. temp. = 80 °C (176 °F), 50 m (165 ft.)
	


1 Minimum installation temperature -45 °C (-49 °F).
Controls

	Product #
	Description
	Qty

	Controller options for roof and gutter for de-icing 

	DS-2C1
	Aerial mounted controller with sensor to detect humidity and temperature, 30A, 100V to 277V
	

	DS-8C1
	Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 
30A, 100V to 277V
	

	DS-9C1
	Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 
2 X 30A, 100V to 277V
	

	EX-50
	50 ft. (15 m) extension kit, with connection fittings for humidity sensor
	

	CDP-2
	Interior controller and display for DS products
	

	ETO21
	Dual-zone electronic controller, 3 X 16A, 120V to 240V
	

	ETF-744/99
	24V outdoor sensor for measuring temperature
	

	ETOR-55
	Gutter sensor to detect humidity with 33 ft. (10 m) cable
	

	Controller options for pipe tracing for use in non-hazardous (ordinary) locations

	ECA-E55-R25HT1
	SPDT, NEMA 4X thermostat in molded aluminum housing, 22A at 120/250/480V, with 10 ft. (3 m) stainless steel bulb and capillary
	

	TPR-L1N-3X-Q101
	SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 3 ft. (1 m) tinned copper bulb 
and capillary
	

	TPR-L1N-10X-Q101
	SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 10 ft. (3 m) tinned copper bulb 
and capillary
	

	TRF115-0051
	SPDT, NEMA 4X thermostat, range -17 °C to 49 °C (0 °F to 120 °F), 25A at 120/208/240/277V, with 5 ft. (1.5 m) stainless bulb 
and capillary
	

	TRF115-0071
	SPDT, NEMA 4X thermostat, range -35 °C to 38 °C (-30 °F to 100 °F), 25A at 120/208/240/277V, with 8 ft. (2.4 m) copper bulb 
and capillary
	

	ELTC-14-RTD1
	Digital temperature control 20A at 90-260V, including 3-wire RTD (Pt-100) sensing element is 5x50mm with 5m of fluoropolymer lead wires, range 0 to 250°C
	

	GPT-130
	Single point heat trace control thermostat NEMA 4X c/w GFEP and a 20 ft. thermistor 30A@100-277V
	

	S1-A
	NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP 

and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet, Modbus and BACnet3 capabilities
	

	S1-B
	NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP 

and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet
	

	GATEWAY-PCKG
	24VDC BACnet gateway assembly with power supply NEMA 4X enclosure with 24VDC transformer for S1 Series
	

	GATEWAY
	24VDC BACnet gateway stand alone for S1 Series
	

	Controller options for pipe tracing for use in non-hazardous (ordinary) and hazardous locations

	TXR-L2S-10-Q101
	SPDT, explosion-proof, NEMA 4, 7 and 9 thermostat, in anodized aluminum housing, 22A at 120/250/480V, 

with 10 ft. (3 m) stainless steel bulb and capillary
	

	TM-1SIH1-E5-RTD-A1
	TraceMateTM I GFCI electronic thermostat for single circuit at 120V
	

	TM-1DIH2-E5-RTD-A1
	TraceMateTM I GFCI electronic thermostat for single circuit at 240/208V
	

	TM-2SIH1-E5-RTD
	TraceMateTM II GFCI electronic thermostat for dual circuit at 120V
	

	TM-2DIH2-E5-RTD
	TraceMateTM II GFCI electronic thermostat for dual circuit at 240/208V
	

	MS-21012
	MasterTrace Single circuit electronic GFCI controller with double pole, 85V to 280V, 30A, with user interface
	

	MS-21022
	MasterTrace Double circuit electronic GFCI controller with single pole, 120V or 277V, 30A, with user interface
	

	RTD-7
	RTD probe for MasterTrace controller
	

	Control panel options

	SR-4CIR-240
	4 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.)
	

	SR-6CIR-240
	6 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.)
	

	SR-8CIR-240
	8 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x20x8 in.)
	

	SR-12CIR-240
	12 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x24x8 in.)
	


1 Requires a ground fault circuit interrupter (GFCI) in the electrical panel.
2 Requires a RTD probe for MasterTrace controller (RTD-7).
3 BACnet IP or MS/TP available via preconfigured SMC gateway, sold separately.
Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electricial Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

