[image: image3.png]AR CerTIFIED®




[image: image4.png]N\
INVERTER
N



[image: image5.png]





Approval Drawings

Series
OTP-O-R32
Olympia R32 Ductless Single Zone Heat Pump
[image: image6.jpg]@gsCOLD

s CLIMATE




[image: image7.png]


 
[image: image8.png]




Features
Operation mode
- 
Cooling, heating, dehumidifying, fan and auto.
Nominal capacity
-
9000, 12000, 18000, 24000 BTU/hr. 
Voltage
-
230/208V, 60 Hz, 1-phase.
Indoor unit
- 
High wall installation, dual side connection.


-
Plastic housing, standard white.

-
Washable filters.

-  A2L leak detection sensor, included.
Outdoor unit
-
Variable speed rotary compressor (INVERTER), with overload protection.


-
Electronic expansion valve for precise control of refrigerant flow.


-
Condenser fins covered with a hydrophilic coating for improved corrosion resistance.


-
Large diameter quiet axial-flow fan for more efficient heat exchange.


-
Smart pan heater to prevent ice formation.


-
Compressor blanket and preheating technology.


-

Installation on aluminum wall bracket or ground stand (optional).
Connection piping
-
Minimum piping length of 10 ft. (3 m).

· Flared connections.

Control 
-
Wireless remote included.

- 
Wired wall controller available.


-
Wi-Fi
-
Set temperature: 16 to 30 °C (61 to 86 °F).

-
Temperature display format °C or °F.
Warranty
-
10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

· Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with condenser replacement if the compressor fails.

Application
-
Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.
[image: image9.png]



Models
	Product #1 
	Indoor Unit
	OARX-H09A-I
	OARX-H12A-I
	OARX-H18A-I
	OARX-H24A-I

	
	Outdoor Unit
	OARX-H09A-O
	OARX-H12A-O
	OARX-H18A-O
	OARX-H24A-O

	Qty
	
	
	
	

	Technical Performance

	Refrigerant type
	
	
	R32
	R32
	R32
	R32

	Voltage
	
	Volts
	230/208
	230/208
	230/208
	230/208

	Cooling capacity
	Nominal
	W (BTU/hr)
	2666 (9100)
	3517 (12000)
	5276 (18000)
	6450 (22000)

	
	Min. – max.
	W (BTU/hr)
	400 - 3800 

(1365 - 12966)
	850 - 4500 

(2900 - 15354)
	1300 - 7500 

(4435 - 25590)
	1700 - 9200 

(5800 - 31400)

	Heating capacity
	Nominal
	W (BTU/hr)
	3106 (10600)
	3575 (12200)
	5450 (18595)
	7000 (24000)

	
	Min. – max.
	W (BTU/hr)
	800 - 5000 

(2730 - 17060)
	900 - 5000 

(3071 - 17060)
	1500 - 7700 

(5118 - 26272)
	1700 - 9700 

(5800 - 33100)

	Used cooling power input
	Nominal
	W
	542
	790
	1256
	1573

	
	Min. – max.
	W
	75 – 1250
	75 - 1250
	150 – 2800 
	265 – 3150

	Used heating power input
	Nominal
	W
	706
	786
	1362
	1803

	
	Min. – max.
	W
	160 – 1650
	250 – 1750
	250 – 3500
	320 – 4800

	Used rated input
	W
	1650
	1750
	3500
	4800

	Rated current
	A
	7.6
	7.8
	16
	21.5

	MCA
	A
	11
	11
	21
	25.5

	Max. over-current protection (MOCP)
	A
	15
	15
	25
	30

	SEER
	-
	30
	28
	27.5
	27

	HSPF
	-
	11.2
	10
	10
	10

	EER
	W/W
	15
	15.52
	13.65
	13.31

	COP
	W/W
	4.4
	4.55
	4
	3.9

	AHRI number
	-
	216472855
	216472856
	216498641
	216498640

	ENERGY STAR 
	-
	(
	(
	(
	(

	Indoor Unit
	
	
	
	

	Dehumidification
	pt/hr (l/hr)
	1.69 (0.80)
	2.96 (1.40)
	3.80 (1.80)
	7.30 (3.50)

	Air flow volume


	cfm
	450 - 860
	600 - 960
	800 - 1250
	600 - 1300

	Sound level


	dB (A)
	23 - 42
	27 - 43
	35 - 49
	36 - 53

	Fan motor power output
	W
	50
	50
	60
	110

	Fan motor RLA
	A
	0.4
	0.4
	0.7
	0.85

	Net weight
	lb (kg)
	33 (15)
	33 (15)
	38.6 (17.5)
	39.6 (18)

	Outdoor Unit
	
	
	
	

	Air flow volume
	cfm
	3000
	3000
	3200
	4500

	Sound level
	dB (A)
	56
	55
	59
	62

	Compressor power input
	W
	757
	757
	1358
	1775

	Compressor LRA
	A
	20
	20
	25
	38

	Compressor RLA
	A
	7.2
	7.2
	14.3
	18

	Fan motor power output
	W
	40
	40
	60
	90

	Fan motor RLA
	A
	1
	1
	1.1
	1.7

	Refrigerant volume (R32)
	oz (g)
	35.27 (1000)
	35.27 (1000)
	47.62 (1350)
	56.44 (1600)

	Net weight
	lb (kg)
	99.2 (45)
	99.2 (45)
	141.1 (64)
	147.7 (67)

	Operating ambient temperature
	Cooling
	°C (°F)
	-29 à 50 (-20 à 122)

	
	Heating
	°C (°F)
	-30 à 30 (-22 à 86)

	Connection Piping/Refrigerant

	Pre-charge length
	ft. (m)
	25 (7.5)
	25 (7.5)
	25 (7.5)
	25 (7.5)

	Additional refrigerant charge
	oz/ft. (g/m)
	0.18 (16)
	0.18 (16)
	0.46 (40)
	0.46 (40)

	Liquid pipe outer diameter 
	in.
	1/4
	1/4
	1/4
	1/4

	Gas pipe outer diameter 
	in.
	1/2
	1/2
	5/8
	5/8

	Maximum height difference
	ft. (m)
	82 (25)
	82 (25)
	82 (25)
	82 (25)

	Maximum total length
	ft. (m)
	131 (40)
	131 (40)
	131 (40)
	131 (40)


1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

[image: image10.png]


[image: image1.jpg]



	Indoor Unit
	L
	H
	D
	A
	B
	C

	
	in.
	mm
	in.
	mm
	in.
	mm
	in.
	mm
	in.
	mm
	in.
	mm

	OARX-H09A-I

OARX-H12A-I
	39 3/16
	970
	13 21/32
	347
	10 1/8
	257
	8 5/64
	205
	22 1/8
	562
	7 
	203

	OARX-H18A-I

OARX-H24A-I
	43 45/64
	1110
	13 21/32
	347
	10 1/8
	257
	10 53/64
	275
	22 1/8
	562
	10 3/4
	273


	Outdoor Unit
	L
	H
	D
	A
	B

	
	in.
	mm
	in.
	mm
	in.
	mm
	in.
	mm
	in.
	mm

	OARX-H09A-O

OARX-H12A-O
	34 3/8
	873
	21 27/32
	555
	14 7/8
	378
	20 25/32
	528
	13 1/2
	343

	OARX-H18A-O


	38 25/32
	985
	26
	660
	15 53/64
	402
	22 7/16
	570
	14 10/16
	371

	OARX-H24A-O


	38 5/8
	1000
	29 3/8
	746
	16 13/16
	427
	24
	610
	15 9/16
	395


Options
See OTP Options section
Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrical Contractor:
	

	Distributor:
	

	Date:
	

	Contact at Ouellet:
	

	Coments:


[image: image2.jpg]



-29˚C�-20˚F





Performance up to 





Up to





-30˚C�-22˚F





30 SEER2





11.2 HSPF2





Indoor Unit





Outdoor Unit





Side View





Front View





Top View





Front View





Side View





Back View








[image: image11.png]\
|

| |

\

=
[ (it Z = \
{{,""{{ﬁ!,,,ﬁgg&?\\\\‘\“ =
AR "ln{""&‘\ \\\\\ \\\\\\\\\ T
\\\\\\\\\\\\\\\\ \‘\}}‘“\‘}“\“\\\\\

\\\\\\\g\\\\\\ W Wuainiiil

S 4

S



180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

[image: image12.png]SmartPan  Crankcase Fin Quiet Smart Smart Auto Auto-Clean Self-
Heater Heater Coating Design Defrosting  Preheating Restart Diagnosis
A -—
*,
3 aflzllo 2
7 N 0
Sleep Turbo Up &Down  Left &Right Timer | Feel Lock Wireless Wi-Fi

Mode Mode Swing Swing Remote

2

AL
safety
sensor

Wall
Controller



[image: image13.png]e

NCOOLING &

Cooling Heating _—




[image: image14.jpg]@DUELLET



