[image: image1.jpg]


[image: image3.emf]









Approval Drawings

Series

OWC-M
Heating Cable for Concrete on Mat

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features

Voltage
-
240/208V, 347V, 1-phase.
Construction
-
Twin conductor heating cable attached to a plastic mat 



with negligible magnetic field.
· Factory installed on mat at 6’’ (15 cm) spacing.

Watt density
-
11W/sq. ft. (120W/sq. m).
Dimension
-
24’’ (0.6 m) wide mat available in several lengths.
Cold lead length
-
8’ 2’’ (2.5 m) cold lead included.
· Optional 50’ (15 m) cold lead available upon request.

Control
-
Two types of control method possible (see instruction manual for details): 



• Surface heating control with electronic thermostat in floor mode (F) and temperature sensor.


•
Ambient heating control with electronic thermostat in ambient mode with floor limit (A or AF) and temperature sensor.

Note: A ground fault circuit interrupter (GFCI) must be used with this heating 

device unless exempted by the applicable national and/or local electrical 

code for the area of installation.
Included materials
-
15' (4.6 m) temperature sensor.

-
Plastic floor fasteners (WC-CLP).

-
Measurement table label (to be placed in for electrical panel).
Installation
-
Never cut or shorten the heating cable.

-
For indoor applications only, residential or commercial. 


-
Installs under a 4" to 6" (10 cm to 15 cm) concrete slab or under a 1.5’’ to 4’’ concrete topping (4 cm to 10 cm).

Note: It’s highly recommended to insulate the concrete slab in order to avoid 

heat loss from below (see instruction manual for all installation details).

-
Compatible with most floor coverings (check with the dealer or manufacturer).

-
Installation with or without metallic structure for reinforced concrete.
Warranty
-
20-year warranty on the heating cable.
Application 
-
Basement, garage, bathroom, kitchen, family room, workshop, pool, shower, entrance way, hospital, hotel, factory, business, restaurant, sunroom, greenhouse, buildings used for housing animals.
Models
	Watts
	Product #
	Covered surface

	Length
	Weight

	
	240/208V
	Qty
	347V
	Qty
	sq. ft.
	sq. m
	ft. in.
	m
	lb
	kg

	150
	OWC-M0150
	
	-
	-
	14.0
	1.3
	6’ 5"
	1.9
	3.0
	1.4

	200
	OWC-M0200
	
	-
	-
	19.0
	1.7
	8' 4"
	2.5
	3.7
	1.7

	300
	OWC-M0300
	
	-
	-
	28.0
	2.6
	12’ 6"
	3.8
	4.0
	1.8

	400
	OWC-M0400
	
	-
	-
	38.0
	3.5
	16’ 8"
	5.1
	4.5
	2.0

	500
	OWC-M0500
	
	-
	-
	46.5
	4.3
	20’ 10"
	6.4
	5.0
	2.3

	600
	OWC-M0600
	
	-
	-
	56.0
	5.2
	25’ 
	7.6
	6.0
	2.7

	700
	OWC-M0700
	
	-
	-
	65.5
	6.1
	29’ 2"
	8.9
	7.0
	3.1

	850
	OWC-M0850
	
	-
	-
	80.0
	7.4
	35’ 5"
	10.8
	8.0
	3.6

	950
	OWC-M0950
	
	-
	-
	89.0
	8.3
	39’ 7"
	12.1
	9.0
	4.0

	1100
	OWC-M1100
	
	-
	-
	103.0
	9.6
	45’ 10"
	14.0
	10.0
	4.5

	1200
	OWC-M1200
	
	-
	-
	113.0
	10.5
	50'
	15.2
	11.0
	5.0

	1300
	OWC-M1300
	
	-
	-
	121.5
	11.3
	54’ 2"
	16.5
	12.0
	5.4

	1400
	OWC-M1400
	
	-
	-
	130.5
	12.1
	58’ 4"
	17.8
	13.0
	6.0

	1500
	OWC-M1500
	
	-
	-
	140.5
	13.1
	62’ 6"
	19.1
	14.0
	6.4

	1600
	OWC-M1600
	
	-
	-
	149.5
	13.9
	66’ 8"
	20.3
	17.0
	7.8

	1700
	OWC-M1700
	
	-
	-
	159.0
	14.8
	70’ 10"
	21.6
	16.0
	7.2

	1850
	OWC-M1850
	
	-
	-
	172.5
	16.0
	77’ 1"
	23.5
	17.0
	7.8

	2000
	OWC-M2000
	
	OWC-M2007
	
	187.5
	17.4
	83’ 4"
	25.4
	18.0
	8.1

	2200
	OWC-M2200
	
	-
	
	206.0
	19.1
	91’ 6"
	27.9
	21.0
	9.5

	2400
	OWC-M2400
	
	OWC-M2407
	
	225.0
	20.9
	100’
	30.5
	23.0
	10.4

	2550
	OWC-M2550
	
	-
	
	239.0
	22.2
	106’ 6"
	32.5
	25.0
	11.3

	2700
	OWC-M2700
	
	OWC-M2707
	
	253.0
	23.5
	112’ 6"
	34.3
	28.0
	12.7

	2850
	OWC-M2850
	
	-
	
	267.0
	24.8
	119’
	36.3
	30.0
	13.6

	3000
	OWC-M3000
	
	OWC-M3007
	
	281.0
	26.1
	125’
	38.1
	32.0
	14.5

	3200
	OWC-M3200
	
	-
	
	300.0
	27.9
	133’ 6"
	40.7
	34.0
	15.4

	3400
	OWC-M3400
	
	OWC-M3407
	
	318.5
	29.6
	141’ 8"
	43.2
	36.0
	16.3

	3600
	OWC-M3600
	
	-
	
	336.0
	31.2
	150’
	45.7
	38.0
	17.2

	3700
	-
	-
	OWC-M3707
	
	346.5
	32.2
	154’ 2
	47.0
	39.0
	17.7

	4000
	-
	-
	OWC-M4007
	
	375.0
	34.8
	166’ 8"
	50.8
	42.0
	19.0



 Does not represent the room surface but rather the area covered by the cable mat including 3” (7.5 cm) spacing between the mat strips but excluding fixed elements to be bypassed and any other required clearances.  

208V = 75% of wattage at 240V.
Options

	Product  # 
Kit
	Product  # 

Factory installed*
	Description
	Qty

	OTM-CC1
	-
	CableCheck – Electrical indicator
	

	KIT-WC-CLP
	-
	Bag of 50 plastic floor fasteners for heating cable on mat
	

	KIT-SP2
	-
	Repair kit 
	

	-
	-502
	Optional 50’ (15 m) cold lead
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 
1 With any OWC order, the accessory OTM-CC can be added free of charge upon costumer request. 
2 Made to order only. Allow additional 9 to 12 weeks lead time.

GFCI control panel with contactors and 24V control transformer

	Product  # 
Kit
	H x W x D

(in.)
	Description
	Qty

	WC-2CIR-208
	16x14x8
	2 circuits 208V 30A
	

	WC-4CIR-208
	20x16x8
	4 circuits 208V 30A
	

	WC-6CIR-208
	20x16x8
	6 circuits 208V 30A
	

	WC-8CIR-208
	24x24x8
	8 circuits 208V 30A
	

	WC-10CIR-208
	24x24x8
	10 circuits 208V 30A
	

	WC-12CIR-208
	24x24x8
	12 circuits 208V 30A
	

	WC-2CIR-240
	16x14x8
	2 circuits 240V 30A
	

	WC-4CIR-240
	20x16x8
	4 circuits 240V 30A
	

	WC-6CIR-240
	24x20x8
	6 circuits 240V 30A
	

	WC-8CIR-240
	24x20x8
	8 circuits 240V 30A
	

	WC-10CIR-240
	24x24x8
	10 circuits 240V 30A
	

	WC-12CIR-240
	24x24x8
	12 circuits 240V 30A
	

	WC-3CIR-347-347
	16x14x8
	3 circuits 347V 24A 
	

	WC-6CIR-347-347
	20x16x8
	6 circuits 347V 24A 
	

	WC-9CIR-600-347
	30x24x8
	9 circuits 600V 24A
	

	WC-12CIR-600-347
	30x24x8
	12 circuits 600V 24A
	


Others

	Type
	Quantity
	Model et description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:








180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

