[image: image1.jpg]


[image: image3.emf]









Approval Drawings

Series

OWC-R
Heating Cable for Concrete in Reel

[image: image4.jpg]@DUELLET



  [image: image2.jpg]




Features

Voltage
-
240/208V, 1-phase.
Construction
-
Twin conductor heating cable with negligible magnetic field.
· Recommended installation – 6’’ (15 cm) spacing.

Watt density
-
11W/sq. ft. (120W/sq. m).
Cold lead length
-
8’ 2’’ (2.5 m) cold lead included.
· Optional 50’ (15 m) cold lead available upon request.
Control
-
Two types of control method possible (see instruction manual for details): 



• Surface heating control with electronic thermostat in floor mode (F) and temperature sensor.


•
Ambient heating control with electronic thermostat in ambient mode with floor limit (A or AF) and temperature sensor.

Note: A ground fault circuit interrupter (GFCI) must be used with this heating 

device unless exempted by the applicable national and/or local electrical 

code for the area of installation).
Included materials
-
15' (4.6 m) temperature sensor.

-
Nylon ties.

-
Measurement table label (to be placed in for electrical panel).
Installation
-
Never cut or shorten the heating cable.

-
For indoor applications only, residential or commercial. 


-
Installs under a 4" to 6" (10 cm to 15 cm) concrete slab or under a 1 1/2’’ to 4’’ 



concrete topping (4 cm to 10 cm).

Note: It’s highly recommended to insulate the concrete slab in order to avoid heat loss from below (see instruction manual for all installation details).

-
Requires a metallic structure or wire mesh for installing the heating cable in reinforced concrete.

-
Compatible with most floor coverings (check with the dealer or manufacturer).
Warranty
-
20-year warranty on the heating cable.
Application 
-
Basement, garage, bathroom, kitchen, family room, workshop, pool, shower, entrance way, hospital, hotel, factory, business, restaurant, sunroom, greenhouse, buildings used for housing animals.
Models
	Watts
	Product #
	Covered Surface1

Spacing 6’’ (15 cm)
	Cable Length
	Weight

	
	240/208V
	Qty
	sq. ft.
	sq. m.
	ft.
	m
	lb
	kg

	300
	OWC-R0300
	
	28.0
	2.6
	56
	17.07
	4.0
	1.8

	500
	OWC-R0500
	
	46.5
	4.3
	93
	28.35
	5.0
	2.3

	700
	OWC-R0700
	
	62.5
	5.8
	125
	38.10
	7.0
	3.1

	950
	OWC-R0950
	
	88.0
	8.2
	176
	53.64
	9.0
	4.0

	1300
	OWC-R1300
	
	125.0
	11.6
	250
	76.20
	12.0
	5.4

	1700
	OWC-R1700
	
	156.0
	14.5
	312
	95.10
	16.0
	7.2

	2000
	OWC-R2000
	
	187.0
	17.4
	374
	114.00
	18.0
	8.1

	2400
	OWC-R2400
	
	218.5
	20.3
	437
	133.20
	23.0
	10.4

	3000
	OWC-R3000
	
	279.5
	26.0
	559
	170.38
	32.0
	14.5

	3400
	OWC-R3400
	
	312.5
	29.03
	625
	190.50
	36.0
	16.3

	3700
	OWC-R37002
	
	341.0
	31.7
	682
	207.87
	39.0
	17.7

	4000
	OWC-R40002
	
	372.5
	34.6
	745
	227.08
	42.0
	19.0


1 Does not represent the room surface but rather the area covered by the cable while leaving a 6” (15 cm) spacing between cables and excluding fixed elements to be bypassed and any other clearance required.  
2 Not compatible with a floor heating thermostat rated for 15A and less. Requires relay with low voltage thermostat.
208V = 75% of wattage at 240V.
Options

	Product  # 

Kit
	Product  # 

Factory installed*
	Description
	Qty

	OTM-CC1
	-
	CableCheck – Electrical indicator
	

	KIT-WC-CLP
	-
	Bag of 50 plastic floor fasteners for heating cable on mat
	

	KIT-SP2
	-
	Repair kit 
	

	-
	-502
	Optional 50’ (15 m) cold lead
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 With any OWC order, the accessory OTM-CC can be added free of charge upon costumer request. 
2 Made to order only. Allow additional 9 to 12 weeks lead time.

GFCI control panel with contactors and 24V control transformer

	Product  # 

Kit
	H x W x D

(in.)
	Description
	Qty

	WC-2CIR-208
	16x14x8
	2 circuits 208V 30A
	

	WC-4CIR-208
	20x16x8
	4 circuits 208V 30A
	

	WC-6CIR-208
	20x16x8
	6 circuits 208V 30A
	

	WC-8CIR-208
	24x24x8
	8 circuits 208V 30A
	

	WC-10CIR-208
	24x24x8
	10 circuits 208V 30A
	

	WC-12CIR-208
	24x24x8
	12 circuits 208V 30A
	

	WC-2CIR-240
	16x14x8
	2 circuits 240V 30A
	

	WC-4CIR-240
	20x16x8
	4 circuits 240V 30A
	

	WC-6CIR-240
	24x20x8
	6 circuits 240V 30A
	

	WC-8CIR-240
	24x20x8
	8 circuits 240V 30A
	

	WC-10CIR-240
	24x24x8
	10 circuits 240V 30A
	

	WC-12CIR-240
	24x24x8
	12 circuits 240V 30A
	

	WC-3CIR-347-347
	16x14x8
	3 circuits 347V 24A 
	

	WC-6CIR-347-347
	20x16x8
	6 circuits 347V 24A 
	

	WC-9CIR-600-347
	30x24x8
	9 circuits 600V 24A
	

	WC-12CIR-600-347
	30x24x8
	12 circuits 600V 24A
	


Others

	Type
	Quantity
	Model and description

Complementary informations
	Volts
	Phase
	Watts
	Length

mm/in.
	Informations

Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Eectrician Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

