[image: image1.png]


[image: image3.emf]









Approval Drawings

Series
OWS-T
Heating Cable for Snow Melting on Mat

[image: image4.jpg]@DUELLET



[image: image2.jpg]




Features
Voltage
-
240/208V, 1-phase.
Construction
-
Series heating cable set, twin conductor type.
· Heating cable held as a mat at regular 3’’ (76 mm) spacing with flexible strips.

· Fluoropolymer/XLPE resistance wire insulation 0.019’’ (0.5 mm) thick.
· Copper shielding (0.823 sq. mm), serves as ground.
· Polyolefin (EPR) outer sheath insulation 0.08’’ (2 mm) thick.
Watt density
-
50W/sq. ft. (538W/sq. m) at 240V, 3’’ (76 mm) spacing.
Dimension
-
24’’ (610 mm) and 36’’ (914 mm) wide mats offered in several lengths.
Cold lead
-  50’ (15 m) long.
· 12 AWG or 14 AWG (according to maximum allowable load).

· PVC outer sheath insulation 0.03’’ (0.76 mm) thick.
· 3/8’’ (9.5 mm) outer diameter.
Included materials
-  Measurements table label (to be placed in electrical panel).
Installation
-
Never cut or shorten the heating cable.
· For outdoor applications only. 

· The heating cable must be completely embedded in concrete, asphalt 
or stone dust under paving.
· Minimum installation temperature -5 °C (23 °F).
· Maximum long-term exposure temperature 105 °C (221 °F).

· Maximum exposure temperature for 10 minutes 220 °C (428 °F).
Warranty
-
10-year warranty on heating cable.
Application
-
Residential driveway, sidewalk, access ramp, underground parking ramp, 
boarding platforms for animals.


 OWS-T 24 in. (610 mm) Wide Mat Models
	Watts
	Product #
	Covered surface

	Mat length
	Cable length

	Weight

	
	208V
	AMP
	Qty
	240V
	AMP
	Qty
	sq. ft.
	sq. m
	ft.
	m
	ft.
	m
	lb
	kg

	500
	OWS-T0508-24
	2.40
	
	OWS-T0500-24
	2.08
	
	11.0
	1.0
	5
	1.5
	43
	13.1
	3.0
	1.4

	1000
	OWS-T1008-24
	4.81
	
	OWS-T1000-24
	4.17
	
	22.0
	2.0
	10
	3.0
	86
	26.2
	5.0
	2.3

	1500
	OWS-T1508-24
	7.21
	
	OWS-T1500-24
	6.25
	
	32.5
	3.0
	15
	4.6
	128
	39.0
	7.0
	3.2

	2000
	OWS-T2008-24
	9.62
	
	OWS-T2000-24
	8.33
	
	43.5
	4.0
	20
	6.1
	171
	52.1
	10.0
	4.5

	2500
	OWS-T2508-24
	12.02
	
	OWS-T2500-24
	10.42
	
	54.0
	5.0
	25
	7.6
	214
	65.2
	12.5
	5.7

	3000
	OWS-T3008-24
	14.42
	
	OWS-T3000-24
	12.50
	
	65.0
	6.0
	30
	9.1
	257
	78.4
	15.0
	6.8

	4000
	OWS-T4008-24
	19.23
	
	OWS-T4000-24
	16.67
	
	86.5
	8.1
	40
	12.2
	342
	104.3
	20.0
	9.1

	5000
	OWS-T5008-24
	24.04
	
	OWS-T5000-24
	20.83
	
	108.5
	10.1
	50
	15.2
	428
	130.5
	25.0
	11.4

	6000
	-
	-
	-
	OWS-T6000-24
	25.00
	
	130.0
	12.1
	60
	18.3
	513
	156.4
	30.0
	13.6


OWS-T 36 in. (914 mm) Wide Mat Models
	Watts
	Product #
	Covered surface1
	Mat length
	Cable length2
	Weight

	
	208V
	AMP
	Qty
	240V
	AMP
	Qty
	sq. ft.
	sq. m
	ft.
	m
	ft.
	m
	lb
	kg

	450
	OWS-T0458-36
	2.16
	
	OWS-T0450-36
	1.88
	
	9.5
	0.9
	3
	0.9
	38
	11.6
	2.5
	1.1

	750
	OWS-T0758-36
	3.61
	
	OWS-T0750-36
	3.13
	
	16.0
	1.5
	5
	1.5
	63
	19.2
	3.5
	1.6

	1050
	OWS-T1058-36
	5.05
	
	OWS-T1050-36
	4.38
	
	22.0
	2.0
	7
	2.1
	88
	26.8
	5.0
	2.3

	1500
	OWS-T1508-36
	7.21
	
	OWS-T1500-36
	6.25
	
	31.5
	2.9
	10
	3.0
	126
	38.4
	8.0
	3.6

	3000
	OWS-T3008-36
	14.42
	
	OWS-T3000-36
	12.50
	
	63.5
	5.9
	20
	6.1
	251
	76.5
	15.0
	6.8

	4500
	OWS-T4508-36
	21.63
	
	OWS-T4500-36
	18.75
	
	95.0
	8.8
	30
	9.1
	377
	114.9
	22.5
	10.2

	6000
	-
	-
	-
	OWS-T6000-36
	25.00
	
	126.5
	11.8
	40
	12.2
	502
	153.0
	30.0
	13.6



 Represents the area covered by the mat including 3’’ (76 mm) spacing between the mat strips but excluding fixed elements to be bypassed and any other required clearances.
2 Represents the total length of the heating cable if it is detached from the flexible strips.
208V = 75% of wattage at 240V.
Installation Options

	Product #
Kit
	Product # 

Factory installed*
	Description
	Qty

	OTM-CC1
	-
	CableCheck – Electrical fault indicator
	

	OW-G82-G
	-
	82 ft. galvanized steel strapping
	

	KIT-SP2
	-
	Repair kit
	

	KIT-SP4
	-
	Extreme case repair kit
	

	
	
	
	

	-
	1002
	Optional 100’ (30 m) cold lead
	

	OWS-CAUT
	-
	Caution playe
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 With any OWS-T order, the accessory OTM-CC can be added free of charge upon costumer request. 
2 Made to order only. Allow additional 9 to 12 weeks lead time.
Control and Sensor Options
	Product #
Kit
	Description
	Amp.
	Volts
	Qty

	DS-2C1
	Aerial mounted sensor with controller to detect humidity and temperature
	30A
	277VAC
	

	ETF-744-99
	24V outdoor sensor for measuring temperature
	-
	24V
	

	ETO21
	Dual-zone electronic controller 
	3 X 16A
	120-240
	

	ETO2-BOX
	Mounting box for dual-zone electronic controller ETO2
	-
	-
	

	ETOG
	Ground sensor to detect humidity and temperature with 33 ft. (10 m) side entry cable
	-
	-
	

	ETOG-56
	Ground sensor to detect humidity and temperature with 80 ft. (25 m) bottom entry cable
	-
	-
	

	ETOK-1
	Mounting tube for ground sensor ETOG-56
	-
	-
	

	ETOR-55
	Gutter sensor to detect humidity with 33 ft. (10 m) cable
	-
	-
	



 Requires a ground fault circuit interrupter (GFCI) in the electrical panel.
GFCI control panel with contactors built-in ETO2 and 120+24V control transformers

	Product  # 
Kit
	H x W x D

(in.)
	Description
	Qty

	WS-4CIR-208
	20x16x8
	4 circuits 208V 30A
	

	WS-6CIR-208
	24x20x8
	6 circuits 208V 30A
	

	WS-8CIR-208
	24x24x8
	8 circuits 208V 30A
	

	WS-12CIR-208
	30x24x8
	12 circuits 208V 30A
	

	WS-4CIR-240
	20x16x8
	4 circuits 240V 30A
	

	WS-6CIR-240
	24x20x8
	6 circuits 240V 30A
	

	WS-8CIR-240
	24x24x8
	8 circuits 240V 30A
	

	WS-12CIR-240
	30x24x8
	12 circuits 240V 30A
	

	WS-3CIR-600-600
	24x24x8
	3 circuits 600V 24A
	

	WS-6CIR-600-600
	30x24x8
	6 circuits 600V 24A
	

	WS-9CIR-600-600
	30x24x8
	9 circuits 600V 24A
	

	WS-12CIR-600-600
	30x30x8
	12 circuits 600V 24A
	

	WS-15CIR-600-600
	36x30x10
	15 circuits 600V 24A
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electricial Contractor:
	

	Distributor:
	

	Date:
	

	Contact in Ouellet:
	

	Comments:











180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

